## Slide 1: Maria’s Restaurant Chapter 4 Section 15

## Slide 2: Deflection and Throw

## Slide 3: Deflection and Throw

## Slide 4: Deflection Question
What is the deflection angle for the diffuser shown?
22O

## Slide 5: Throw Question
What is the throw width and velocity at 25 feet?
50 feet per minute and approximately 15 feet wide (total width 7.5 per side).

## Slide 6
Maria’s Restaurant Diffuser Throw Zone 1
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 7
Maria’s Restaurant Diffuser Throw Zone 2
(one grid square = one ft2)
66 ft.
25 ft.
Zone 1
EX. Hood
Zone 2
Zone 2 Constant Volume 3,200 CFM
Stage 1 Return: 1,300 CFM
Stage 2 Return: 3,100 CFM
Zone 1
Supply Diffuser 550 CFM
5 Supply Diffusers 530 CFM Each
6 Supply Diffusers 400 CFM Each
Zone 1 Constant Volume 2,400 CFM
Return: 1,711 CFM
A
B
C
F
D
E
G
H
A
B
C
D
E
G
F
H

## Slide 8: Return Grille

## Slide 9: Filter Design
The filtered airflow for Zones 1 & 2 are maximized in the economizer mode, at 2,400 CFM and 3,200 CFM respectively. Based on information found in our selected filters capacity and dimension tables: For Zones 1 & 2, the designer allowed a 0.1 IWC of pressure drop for the filters.

## Slide 10: Filter Considerations
Zone 1: 2,400 CFM ÷ 200 FPM = 12 ft2
Zone 2: 3,200 CFM ÷ 200 FPM = 16 ft2

## Slide 11: Filter Size
The more common approach would be to penalize
the overall operating efficiency by increasing the
blower size and fan speed to overcome the filter
resistance. Looking again at Figure 28, a face
velocity of 625 FPM would double the pressure
drop for the entire duct system to 1.2”. In this
case, the filter surface areas would be decreased
to:
Zone 1: 2,400 CFM ÷ 625 FPM = 3.84 ft2
Zone 2: 3,200 CFM ÷ 625 FPM = 5.12 ft2

## Slide 12: Filter Considerations 1
What size filter would be needed if the
CFM value was 4,200 and the design IWC
was 0.20?
About
344 fpm
4,200 ÷ 344 = 12.21 Sq. Ft.

## Slide 13: Filter Considerations 1
What size filter would be needed if the
CFM value was 3,200 and the design IWC
was 0.20?
About
344 fpm
3,200 ÷ 344 = 9.3 Sq. Ft.

## Slide 14: Return Filter Question 2
Based on the XYZ filter chart used in the previous two charts, what will the pressure drop and face velocity be if a 27 × 24 filter is used for Maria’s restaurant Zone 1?

## Slide 15: Return Filter Question 2
Based on the XYZ filter chart used in the previous two charts, what will the pressure drop and face velocity be if a 27 × 24 filter is used for Maria’s restaurant Zone 1’s 2,400 CFM?
(27 × 24) ÷ 144 = Square feet of filter area = 4.5
2,400 CFM ÷ 4.5 ft2 = 533 feet per minute

## Slide 16: Resistance in IWC Zone 1
533 feet per minute
About
533 fpm
About
0.48 IWC

## Slide 17: Return Filter Question 2
Based on the XYZ filter chart used in the previous two charts, what will the pressure drop and face velocity be if a 27 × 24 filter is used for Maria’s restaurant Zone 2’s 3,200 CFM?
(27 × 24) ÷ 144 = Square feet of filter area = 4.5
3,200 CFM ÷ 4.5 ft2 = 711 feet per minute

## Slide 18: Resistance in IWC Zone 1
711 feet per minute
Off of the chart ….
Never go beyond the chart

## Slide 19: Field Notes
Unfortunately, it is not unusual to find a supply register with a design throw and angle that will cause someone to feel like they are sitting in a draft. Remember, simply throttling them down is not a solution. The author once found an office where 4 out of 5 diffusers were shut down causing the system to force the air through the last diffuser. The lady sitting in the strong breeze under that remaining noisy diffuser said she was the one who was always wanting it cooler so she didn’t feel she could complain. When all of the throw angles and CFM were properly set everyone was comfortable and the system had the correct airflow. Finally, it is way too common to find a filter that is too small for the HVAC system. Installers rarely check the filter area pressure drop design requirement and will install a return grille based on the duct size. Thus, the design external static pressure for the system will be high with an extremely high (negative value) value for the return duct measurement. You have probably seen in the field a properly designed system where the filter box area is much larger than the return duct.