## Slide 1: Maria’s Restaurant Lesson 17 Appendix A Zone 1 Equipment Loads

## Slide 2: Maria’s Restaurant
Maria’s

## Slide 3
Maria’s Restaurant Design
(Staff: Maria & 6 Employees each shift. Glass Store Front and front door)
66 ft.
25 ft.
F1
R1
S1
DW
C1
CT/O
C2
C3
SP
Fry
R2
F2
Woman’s
Restroom
1 handicap
1 standard
Men’s
Restroom
1 handicap
1 urinal
H1
Bar
Ice
C6
Counter
S3
C7
Bar 12 X 10
Seating 12
Restaurant 33 X 15
11 X 4 & 11 X 6
Seating 58
R3
R4
B1
Shelv.
S2
SK
B = Beverage Area R = Refrigerator (blue walk in
C = Counter S = Sink; S1 Hand; S2 3 Pot; S3 Bar
CT = 4 burner plus flat top over ovens SK= Steam Kettle
DW = Dishwasher SP = Salad/cold Prep table
F = Freezer (blue walk in) H1 = Hot Prep Table with Heat Lamp Shelf
Shelv..
Shelving/Storage
WH
S1
B2
ZONE 1

## Slide 4: Zone 1 Restaurant & Bar Area Equipment
For Maria’s Restaurant, the Restaurant and Bar area equipment’s total Btuh value is: 22,186 Btuh
The following presentation shows how the total Btuh was calculated for each piece of equipment shown on the drawing, and then added to some small appliances and restaurant equipment not shown on the drawing Maria has specified electrical circuits for.

## Slide 5: Bar Refrigerator
Manual N Table 6E
Refrigerator 5 to 25 Cu. ft. per 10 Cuft of space 1,670
Rated at 23.8 Cu. ft.
23.8 ÷ 10 = 2.38 Thus; 2.38 x 1,670 = 3,975

## Slide 6: Beer Keg Refrigerator
Manual N Table 6E
Refrigerator 5 to 25 Cuft: per 10 Cuft of space 1,670
Rated at 19.8 Cuft;
1.98 x 1,670 = 3,307

## Slide 7: Refrigerator Cubic Foot to Btuh 1
Find Btuh for a 24 Cu. ft. refrigerator.
Manual N Table 6E
Refrigerator 5 to 25 Cu. ft. per 10 Cu. ft. of space 1,670
(24 ÷ 10) × 1,670 = 4,008 Btuh

## Slide 8: Refrigerator Cubic Foot to Btuh 2
Find Btuh for a 24 Cu. ft. refrigerator.
Manual N Table 6E
Refrigerator 5 to 25 Cu. ft. per 10 Cu. ft. of space 1,670
(6 ÷ 10) × 1,670 = 1,002 Btuh

## Slide 9: Bar Icemaker
Manual N Table 6E
Ice Maker 110 lb per day sensible no hood; 6,420 Btuh
Approximate: 65 ÷ 110 X 6,420 = 3,794 Btuh

## Slide 10: 2-308 lb Ice Makers/ Drink Servers (Remote Condenser Air Cooled)
Dimensions
W X D X H
22 X 24 x 24
No appreciable Btuh

## Slide 11: Some Other Small Electronic Equipment
Manual N Table 6 C, All without hood in Btuh:
(sensible + latent where applicable)
2 Cash Registers = 400 Btuh
1 Small Desktop Printer Idle = 35 Watts (119 Btuh)
1 Desktop Copier Idle = 20 Watts (68 Btuh)
9 Customer computers/devices = 495 watts
1,689 Btuh (Continuous Usage/ Customers)
Total Small Appliance in Bar Load = 2,276 Btuh
Note: Watts X 3.412 = Btuh

## Slide 12: Watts to Btuh
How many Btuh will be equivalent to six 300 watt incandescent light bulbs?
Watts = 6 × 300 = 1,800
Watts × 3.412 = Btuh
Btuh = 1,800 × 3.412 = 6,142 Btuh

## Slide 13: Amps & Volts to Watts & Btuh 1
For single-phase equipment:
Watts = Amps × Power Factor × Voltage
Find the Watts for a 10 h.p. single phase motor operating at 230 Volts and 50 amps (use PF of 0.85)
Watts = Amps × Power Factor × Voltage
Watts = 50 × 0.85 × 230 = 9,775 Btuh

## Slide 14: Amps & Volts to Watts & Btuh 2
For three-phase equipment:
Watts = Amps × Power Factor × Voltage × 1.732
Find the Watts for a 10 h.p. 3 phase motor operating at 460V and 14 amps (use PF of .85)
Watts = Amps × Power Factor × Voltage × 1.732
Watts = 14 × 0.85 × 460 × 1.732 = 9,480 Watts

## Slide 15: Some Other Small Food Equipment (Bar Area)
Manual N Table 6, All without hood in Btuh:
(sensible + latent where applicable)
2 Coffee Brewers 12 cup 2 Burners (6E) =
2 X (1,910 + 1,810) = 7,440 Btuh
Food Processor 2-3 Qt (6E) = 1,770 Btuh
Blender 2-6 Qt (6E) = 1,000 + 500 = 1,500Btuh
Total Bar Small Appliance Load = 5530 + 5180 Btuh
(10,710 Btuh)

## Slide 16: Total Bar/Entrance Equipment Load (Zone 1)
Refrigeration: 3,975 Btuh
Refrigeration: 3,307 Btuh
Ice Making: 3,794 Btuh
Small Appl.: 5,530 + 5180 10,710 Btuh
Small Electronic Appliances: 2,276 Btuh
Total: 24,062 Btuh
Total latent Load: 5,530 Btuh

## Slide 17: Lighting Specifications
ASHRAE 90.1 2010
Zone 1
Dinning & Bar Wattage per ft2 = 0.90
1,117 ft2 X 0.90 = 1,005 Watts
Note: 1,005 Watts X 3.412 = 3429 Btuh

## Slide 18: Zone 1 Manual N

## Slide 19: Internal Loads

## Slide 20: Zone 1 Load Summary

## Slide 21: Zone 1 Load Summary Denver

## Slide 22: Field Notes
Unfortunately, most building owners do not consider the HVAC system when they remodel. It is not unusual to find thermostats/sensors in sections they do not control, or up in ceilings shoved out of site. The technician was called out because the employee kitchen was too hot year round. The building had a variable air volume system (VAV) with reheats for the perimeter areas. The kitchen was in an internal area so it was always supplied with air that was 65F (in the winter) or cooler (55F in the summer). The technician noted the kitchen was fairly new and that a controlling thermostat/sensor was not present in the room. Since the kitchen was added without considering the HVAC system: the recommendation was for a load calculation to be done based on the newly added kitchen equipment, and that the kitchen area be made into a separate zone on the VAV system, with its own control. This change would require moving a thermostat/sensor and a duct modification, along with an air balance for two VAVs.