## Slide 1: Day 1 Part 3 Technician’s Guide & Workbook for Home Evaluation and Performance Improvement

## Slide 2: Math Review CAZ Volume and Air Free CO PPM Calculations

## Slide 3: CAZ Area Volume

## Slide 4: CAZ Volume Sample Problem 1
“Standard Method” Sample Problem
A 12,000 ft2 home with 9 ft ceilings according to the blower door test has 0.50 ACH and a 148,000 Btuh gas furnace. Is there enough air leakage to support safe combustion?
First the ft3 is calculated:
12,000 ft2 x 9 ft = 108,000 ft3

## Slide 5: Sample Problem 1
“Standard Method” Sample Problem
A 12,000 ft2 home with 9 ft ceilings according to the blower door test has 0.50 ACH and a 148,000 Btuh gas furnace. Is there enough air leakage to support safe combustion?
First the ft3 is calculated:
12,000 ft2 x 9 ft = 108,000 ft3

## Slide 6: Sample Problem 1
Next divide 108,000ft3 by 50ft3 per 1000 Btuh = 648 (how many 50ft3 areas of makeup air per hour there are in the home)
Next multiply the 648 by 1000 Btu to get the maximum combustion appliance total for the home:
648 X 1000 = 648,000

## Slide 7: Sample Problem 1
The Btuh allowable for this leakage rate and home area is 648,000 Btuh
This leaky home could easily support the combustion air needs of the 148,000 Btuh Furnace

## Slide 8: Sample Problem 1
The Btuh allowable for this leakage rate and home area is 648,000 Btuh
This leaky home could easily support the combustion air needs of the 148,000 Btuh Furnace

## Slide 9: Sample Problem 2
“Standard Method” Sample Problem
A 1,500 ft2 home with 8 ft ceilings according to the blower door test has 0.41 ACH and a 200,000 Btuh gas furnace. Is there enough air leakage to support safe combustion?
First the ft3 is calculated:
1,500 ft2 x 8 ft = 12,000 ft3

## Slide 10: Sample Problem 2
Next divide 12,000ft3 by 50ft3 per 1000 Btuh = 240 (how many 50ft3 areas of makeup air per hour there are in the home)
Next multiply the 240 by 1000 Btu to get the maximum combustion appliance total for the home:
240 X 1000 = 240,000

## Slide 11: Sample Problem 2
The Btuh allowable for this leakage rate and home area is 240,000 Btuh
This leaky home could easily support the combustion air needs of the 200,000 Btuh Furnace

## Slide 12: Sample Problem 2
The Btuh allowable for this leakage rate and home area is 240,000 Btuh
This leaky home could easily support the combustion air needs of the 200,000 Btuh Furnace

## Slide 13: National Fuel Gas Code (NFG) §9.3
“Formula Method”
Where the infiltration rate is known and the ACH is less than 0.60: the minimum required volume can be calculated using one of two formulas.
The first is for appliances other than fan-assisted.
The second is for fan-assisted appliances.

## Slide 14: Other Than Fan Assisted Formula
Naturally vented appliance (boiler or furnace) formula:
Required volume ≥ [21ft3 X all appliances input Btuh] ÷ [ACH X 1,000 Btuh]

## Slide 15: Fan Assisted Formula
Fan assisted appliance (boiler or furnace) formula:
Required volume ≥ [15ft3 X for the fan assisted appliance input Btuh] ÷ [ACH X 1,000 Btuh]

## Slide 16: Sample Problem 3
A 12,000 ft2 home with 9 ft ceilings according to the blower door test has 0.50 ACH and a fan-assisted 148,000 Btuh gas furnace, a 48,000 Btuh oven, and a 60,000 Btuh domestic water heater. Will combustion ventilation air need to be added?
Note: ACH ˂ 0.60
First plug the numbers into the fan assisted formula to calculate the area for the furnace:
Required volume ≥ [15ft3 X 148,000 Btuh] ÷ [0.50 X 1,000 Btuh] ≥ 4,440ft3

## Slide 17: Sample Problem 3
A 12,000 ft2 home with 9 ft ceilings according to the blower door test has 0.50 ACH and a fan-assisted 148,000 Btuh gas furnace, a 48,000 Btuh oven, and a 60,000 Btuh domestic water heater. Will combustion ventilation air need to be added?
Note: ACH ˂ 0.60
First plug the numbers into the fan assisted formula to calculate the area for the furnace:
Required volume ≥ [15ft3 X 148,000 Btuh] ÷ [0.50 X 1,000 Btuh] ≥ 4,440ft3

## Slide 18: Sample Problem 3
Next do the calculation using the formula for the naturally vented appliances:
Required volume ≥ [21ft3 X (60,000 + 48,000)] ÷ [0.50 X 1,000 Btuh] ≥ 4,536ft3
Next, add up the two for the total required volume:
4,440ft3 + 4,536ft3 = 8,970 ft3

## Slide 19: Sample Problem 3
Next do the calculation using the formula for the naturally vented appliances:
Required volume ≥ [21ft3 X (60,000 + 48,000)] ÷ [0.50 X 1,000 Btuh] ≥ 4,536ft3
Next, add up the two for the total required volume:
4,440ft3 + 4,536ft3 = 8,970 ft3
12,000 ft2 x 9 ft. = 108,000 ft3

## Slide 20: Sample Problem 4
A 12,000 ft2 home with 9 ft ceilings according to the blower door test has 0.03 ACH and a fan-assisted 148,000 Btuh gas furnace, a 48,000 Btuh oven, and a 60,000 Btuh domestic water heater. Will combustion ventilation air need to be added?
Note: ACH ˂ 0.60

## Slide 21: Sample Problem 4
A 12,000 ft2 home with 9 ft ceilings according to the blower door test has 0.03 ACH and a fan-assisted 148,000 Btuh gas furnace, a 48,000 Btuh oven, and a 60,000 Btuh domestic water heater. Will combustion ventilation air need to be added?
Note: ACH ˂ 0.60
First plug the numbers into the fan assisted formula to calculate the area for the furnace:
Required volume ≥ [15ft3 X 148,000 Btuh] ÷ [0.03 X 1,000 Btuh] ≥ 74,000 ft3

## Slide 22: Sample Problem 4
Next do the calculation using the formula for the naturally vented appliances:
Required volume ≥ [21ft3 X (60,000 + 48,000)] ÷ [0.03 X 1,000 Btuh] ≥ 75,600 ft3

## Slide 23: Sample Problem 4
Next do the calculation using the formula for the naturally vented appliances:
Required volume ≥ [21ft3 X (60,000 + 48,000)] ÷ [0.03 X 1,000 Btuh] ≥ 75,600 ft3
Next, add up the two for the total required volume:
74,000 ft3 + 75,600 ft3 = 149,600 ft3

## Slide 24: Sample Problem 4
Next do the calculation using the formula for the naturally vented appliances:
Required volume ≥ [21ft3 X (60,000 + 48,000)] ÷ [0.03 X 1,000 Btuh] ≥ 75,600 ft3
Next, add up the two for the total required volume:
74,000 ft3 + 75,600 ft3 = 149,600 ft3
12,000 ft2 x 9 ft. = 108,000 ft3

## Slide 25: Air Free CO PPM

## Slide 26: CO Verification
The Carbon Monoxide, air-free ppm may be calculated using one of the following formulas and the data from Table 1,
COAFppm = (UCO2 ÷ CO2) x CO
Or
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm

## Slide 27: CO Verification
The Carbon Monoxide, air-free ppm may be calculated using one of the following formulas and the data from Table 1,
COAFppm = (UCO2 ÷ CO2) x CO ACH ˃ 0.40
Or
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm

## Slide 28: CO Verification
The Carbon Monoxide, air-free ppm may be calculated using one of the following formulas and the data from Table 1,
COAFppm = (UCO2 ÷ CO2) x CO ACH ˃ 0.40
Or
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm ACH ˂ 0.60

## Slide 29: CO Verification
COAFppm = Carbon Monoxide, air-free ppm.
CO2 = The measured concentration of carbon dioxide in combustion products in percent.
COppm = The measured concentration of carbon monoxide in combustion products in percent.
O2 = The measured percentage of oxygen in the combustion gas.
UCO2 = The ultimate concentration of carbon dioxide for the fuel being burned in percent (for natural gas 12.2% and for propane 14.0%).

## Slide 30: Sample Problem 1
A Technician measured the CO2 at 10% by volume in the exhaust gas, and the CO at 150 ppm in the exhaust gas of a vented room heater using propane gas (ACH = 0.50). Does it meet the 200 ppm table value for that appliance?
COAFppm = (UCO2 ÷ CO2) x CO
Thus: COAFppm = (14.0 ÷ 10) x 150 = 210

## Slide 31: Sample Problem 1
COAFppm = (UCO2 ÷ CO2) x CO
Thus: COAFppm = (14.0 ÷ 10) x 150 = 210
14 ÷ 10 = 1.4

## Slide 32: Sample Problem 1
COAFppm = (UCO2 ÷ CO2) x CO
Thus: COAFppm = (14.0 ÷ 10) x 150 = 210
14 ÷ 10 = 1.4
And
1.4 x 150 =

## Slide 33: Sample Problem 1
COAFppm = (UCO2 ÷ CO2) x CO
Thus: COAFppm = (14.0 ÷ 10) x 150 = 210
14 ÷ 10 = 1.4
And
1.4 x 150 = 210

## Slide 34: Sample Problem 1
Appliance | Threshold Limit
Central furnace (all catagories) | 400 ppm air free*
Floor furnace | 400 ppm air free
Gravity furnace | 400 ppm air free
Wall furnace (BIV) | 200 ppm air free
Wall furnace (direct vent) | 400 ppm air free
Vented room heater | 200 ppm air free
Vent-free room heater | 200 ppm air free
Water heater | 200 ppm air free
Oven/boiler | 225 ppm as measured
Top burner | 25 ppm as measured (per burner)
Refrigerator | 25 ppm as measured
Gas log (gas fireplace) | 25 ppm as measured in vent
Gas log (installed in wood burning fireplace) | 400 ppm air free in firebox
This table is provided by permission of the American Gas Association. | 
*Air free emission levels are based on a mathematical equation (involving carbon monoxide and oxygen or carbon monoxide readings) to convert an actual diluted flue gas carbon monoxide testing sample to an undiluted air free flue gas carbon level utilized in the appliance certification standards. | 

## Slide 35: Sample Problem 1
Appliance | Threshold Limit
Central furnace (all catagories) | 400 ppm air free*
Floor furnace | 400 ppm air free
Gravity furnace | 400 ppm air free
Wall furnace (BIV) | 200 ppm air free
Wall furnace (direct vent) | 400 ppm air free
Vented room heater | 200 ppm air free
Vent-free room heater | 200 ppm air free
Water heater | 200 ppm air free
Oven/boiler | 225 ppm as measured
Top burner | 25 ppm as measured (per burner)
Refrigerator | 25 ppm as measured
Gas log (gas fireplace) | 25 ppm as measured in vent
Gas log (installed in wood burning fireplace) | 400 ppm air free in firebox
This table is provided by permission of the American Gas Association. | 
*Air free emission levels are based on a mathematical equation (involving carbon monoxide and oxygen or carbon monoxide readings) to convert an actual diluted flue gas carbon monoxide testing sample to an undiluted air free flue gas carbon level utilized in the appliance certification standards. | 

## Slide 36: Sample Problem 1
Since the calculated free air PPM vale of 210 is higher than the table allowable value of 200: this appliance fails.
This would call for the equipment to be repaired by an expert.

## Slide 37: Sample Problem 2
A Technician measured the O2 at 10% by volume in the exhaust gas, and the CO at 80 ppm in the exhaust gas of a floor furnace using natural gas (ACH = 39). Does it meet the 400 ppm table value?
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm

## Slide 38: Sample Problem 2
A Technician measured the O2 at 10% by volume in the exhaust gas, and the CO at 80 ppm in the exhaust gas of a floor furnace using natural gas (ACH = 39). Does it meet the 400 ppm table value?
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm
Thus: COAFppm [20.9 ÷ (20.9 - 10)] x 80 = 153

## Slide 39: Sample Problem 2
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm
Thus: COAFppm [20.9 ÷ (20.9 - 10)] x 80 = 153.39
20.9 – 10 = 10.9

## Slide 40: Sample Problem 2
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm
Thus: COAFppm [20.9 ÷ (20.9 - 10)] x 80 = 153.39
20.9 – 10 = 10.9
And
20.9 ÷ 10.9 = 1.917

## Slide 41: Sample Problem 2
COAFppm = [20.9 ÷ (20.9 - O2)] x COppm
Thus: COAFppm [20.9 ÷ (20.9 - 10)] x 80 = 153
20.9 – 10 = 10.9
And
20.9 ÷ 10.9 = 1.917
And
1.917 x 80 = 153

## Slide 42: Sample Problem 2
Appliance | Threshold Limit
Central furnace (all catagories) | 400 ppm air free*
Floor furnace | 400 ppm air free
Gravity furnace | 400 ppm air free
Wall furnace (BIV) | 200 ppm air free
Wall furnace (direct vent) | 400 ppm air free
Vented room heater | 200 ppm air free
Vent-free room heater | 200 ppm air free
Water heater | 200 ppm air free
Oven/boiler | 225 ppm as measured
Top burner | 25 ppm as measured (per burner)
Refrigerator | 25 ppm as measured
Gas log (gas fireplace) | 25 ppm as measured in vent
Gas log (installed in wood burning fireplace) | 400 ppm air free in firebox
This table is provided by permission of the American Gas Association. | 
*Air free emission levels are based on a mathematical equation (involving carbon monoxide and oxygen or carbon monoxide readings) to convert an actual diluted flue gas carbon monoxide testing sample to an undiluted air free flue gas carbon level utilized in the appliance certification standards. | 

## Slide 43: Sample Problem 2
Appliance | Threshold Limit
Central furnace (all catagories) | 400 ppm air free*
Floor furnace | 400 ppm air free
Gravity furnace | 400 ppm air free
Wall furnace (BIV) | 200 ppm air free
Wall furnace (direct vent) | 400 ppm air free
Vented room heater | 200 ppm air free
Vent-free room heater | 200 ppm air free
Water heater | 200 ppm air free
Oven/boiler | 225 ppm as measured
Top burner | 25 ppm as measured (per burner)
Refrigerator | 25 ppm as measured
Gas log (gas fireplace) | 25 ppm as measured in vent
Gas log (installed in wood burning fireplace) | 400 ppm air free in firebox
This table is provided by permission of the American Gas Association. | 
*Air free emission levels are based on a mathematical equation (involving carbon monoxide and oxygen or carbon monoxide readings) to convert an actual diluted flue gas carbon monoxide testing sample to an undiluted air free flue gas carbon level utilized in the appliance certification standards. | 

## Slide 44: Sample Problem 2
Since the calculated free air PPM vale of 153ppm is lower than the table allowable value of 400ppm: this appliance passes.