## Slide 1: Day 2 Part 1 Technician’s Guide & Workbook for Home Evaluation and Performance Improvement

## Slide 2: 3.0 Comprehensive Performance Audit Fossil Fuel Appliances Health & Safety 3.2

## Slide 3: Combustion Ventilation Sizing

## Slide 4: Indoor Openings Sizes and Locations
Five rules based on National Code requirements:
Openings must have a minimum free area of 1 in2 per 1000 Btuh based on the total Btuh input value.
One opening must be within 12” of the top of the closet (enclosed space).
One opening must be within 12” of the bottom of the closet (enclosed space).

## Slide 5: Indoor Openings Sizes and Locations

## Slide 6: Indoor Openings Sizes and Locations
Spaces can be combined as part of the same total area when they are connected by openings in doors or floors having open free areas of 2 in2 per 1,000 Btuh based on the total Btuh input value.
The minimum opening size for air openings must be 3” or larger. That requirement is interpreted as meaning an opening of 3”by 3”. So, a door with a two inch undercut would not count but one with a three inch undercut would.

## Slide 7: Sample Question
If there were no indoor openings in a home between a small equipment closet containing a total of 200,000 Btuh’s in equipment, what size opening is required for the equipment?
First: divide Btuh by 1000:
200,000 ÷ 1000 = 200

## Slide 8: Sample Question
200 is our multiplier for the small equipment closet’s required open area for ventilation.
Next:
200 X 2 in2 = 400 in2 open area for the
Finally, 400 in2 ÷ 144 = 2.7777….. Or 2.8 ft2

## Slide 9: Outdoor Combustion Air
Acceptable Type 1: Two Permanent Openings 5 rules:
Openings in vertical ducting must have a minimum free area of 1 in2 per 4000 Btuh based on the total Btuh input value.
Openings in horizontal ducting must have a minimum free area of 1 in2 per 1000 Btuh based on the total Btuh input value.

## Slide 10: Outdoor Combustion Air
Two Permanent Openings 5 rules continued:
One opening must be within 12” of the top of the closet (enclosed space).
One opening must be within 12” of the bottom of the closet (enclosed space).
Spaces can be combined as part of the same total area when they are connected by openings in doors or floors having open free areas of 2 in2 per 1000 Btuh based on the total Btuh input value.

## Slide 11: Outdoor Combustion Air
Acceptable Type 2: One Permanent Opening 4 rules:
One permanent opening within 12” of the top of the enclosed space.
Appliances must have a clearance of 1” from the sides and back and 6” from the front.

## Slide 12: Outdoor Combustion Air
One Permanent Openings 4 rules continued:
Openings in ducting must have a minimum free area of 1 in2 per 3,000 Btuh based on the total Btuh input value of all of the appliances in the enclosed space.
When there is more than one vent connector the size of the opening must be equal to or larger than the area of the vent pipes.

## Slide 13: Sample Calculation
If there were two existing vents and the one on the hot water heater was 3” round and the one on the furnace was 4” round. Is the 6” round vent coming out of the ceiling 11” large enough to handle both of the smaller exhaust vents?
First calculate the area of each existing vent:
A = πr2 and, r = ½ of the diameter

## Slide 14: Sample Calculation
First calculate the area of each existing vent:
A = πr2 and, r = ½ of the diameter
Next we take the 1.5” radius and a 2” radius vents and calculate their areas and add them up:
(3.14 X 1.52) + (3.14 X 22) = 19.625in2. Thus, the minimum area for the two added together is 19.625in2

## Slide 15: Sample Calculation
Does the 6” duct that they are attached in a home to meet the requirement?
First calculate the area of the 6” duct: 3.14 X 32 = 28.26 in2 :
Thus, the six inch inside diameter round duct installed is large enough and it meets the 19.625in2 minimum requirement.

## Slide 16: Combination Indoor and Outdoor Combustion Air
All of the directions previously provided in this section must be followed for the individual opening types, sizes and locations (including equipment spacing requirements). The calculation is done by finding ratios for each type of combustion air and using them to find the size opening needed to provide the remaining outside air. The additional outside required and the ratios are calculated using these formulas:

## Slide 17: Combination Indoor and Outdoor Combustion Air
The additional outside required and the ratios are calculated using these formulas:
Interior space volume in ft3 ÷ the required volume = ratio of interior spaces (to the amount of air required if it is above 1 no outside air is required)
Outdoor size reduction factor = 1 - ratio of interior spaces
Outdoor minimum size opening must be in accordance with the two permanent or the one permanent size procedures previous provided.

## Slide 18: Sample Calculation
Sample Calculation Part A:
If there was a 9,000ft3 interior volume connected to the combustion area in a home, where the requirement was for a 12,000ft3 area based on the formulas what would the ratio of interior spaces be?
Ratio of interior spaces = 9,000 ÷ 12,000 = 0.75

## Slide 19: Sample Calculation
Sample Job 5 Part B:
Find the outdoor size reduction factor using the 0.75 calculated above as the ratio of interior spaces:
Outdoor size reduction = 1 – 0.75 = 0.25.
The outdoor size reduction factor calculated using the formulas is multiplied times the size reduction factor to get the required outside air opening/ducting.

## Slide 20: Sample Calculation
Thus, for the Sample Calculation’s 5 parts A&B, the outside air design opening size can be reduced by 75%. Note: it must still have a minimum opening size of 3” (round).

## Slide 21: Sample Calculation
The easy way to remember this is you need 100% of the calculated required outside air for safe combustion. So if you need 12,000ft3 in total and there is 9000ft3 of the requirement covered by the open area you need to have an outside air opening that will allow in 3,000ft3. Since an Acceptable Type 2: One Permanent Opening requires 1 in2 per 3000 Btuh you would need to have a 3” round opening to meet the minimum size requirement.

## Slide 22: Other Requirements
Engineered combustion air installations must be approved by the authority having jurisdiction
For Mechanical (fan) combustion air supply systems. Combustion air must come from the outside at a minimum rate of 0.35ft3 per minute

## Slide 23: Other Requirements
Additional air equivalent to exhausted air is required where exhaust fans are present
An interlock with the appliance and the exhaust air fan is required
When the combustion air is brought in with the required ventilation air it is to be added to the total required for ventilation

## Slide 24: Screen, Louver, and Grille Sizing
Screens, louvers, and Grilles have the 5 following sizing requirements:
Manufacturer’s free area should be used to determine the opening size
When free area is unknown wood louvers will be considered to have a 25% opening

## Slide 25: Screen, Louver, and Grille Sizing
When free area is unknown metal louvers will be considered to have a 75% opening
Pest screens will have a minimum mesh size of ¼”.
Motorized louvers must have an interlock switch with the appliance to keep the burner from operating when they are closed

## Slide 26: Acceptable Documentation
Written or recorded records of Combustion Appliance Zone Area Measurement Calculations.
And
Written or recorded records that other outdoor air requirements covered in this section have been met.
Or
Written or recorded records of homeowner notification that items not in compliance with the other outdoor air requirements covered in this section have not been met.

## Slide 27: Combustion Air Ducting Inspection

## Slide 28: Combustion Air Ducting
Ducting for combustion air must meet the following 8 requirements:
Must be constructed of galvanized steel or have equivalent strength, rigidity, and resistance to corrosion.
Where more than one fire block is removed, joint space, and open stud areas may be used for running the duct.
Duct must end in a location where it is not going to be blocked off.

## Slide 29: Combustion Air Ducting
Duct can only be used for one space…if there are two different equipment rooms two separate duct systems are needed.
One duct cannot be used as both the upper and lower duct in an Acceptable Type 1: Two Permanent Openings system
Ducts terminating in a vented attic space must not have a screen on them.

## Slide 30: Combustion Air Ducting
Horizontal ducts must not slope down towards the combustion air’s source.
Cavity space in a building or extra piping in a chimney cannot be used to supply combustion air.

## Slide 31: Combustion Air Ducting
Solid fuel burning direct vent appliances are allowed to be vented in accordance with the manufacturer’s directions.

## Slide 32: Combustion Air Ducting
The finished ground level must be at least 12” below the combustion air intake. In many areas code may require them to be higher due to annual snowfall

## Slide 33: Combustion Air Ducting
The finished ground level must be at least 12” below the combustion air intake. In many areas code may require them to be higher due to annual snowfall

## Slide 34: Atmospherically Vented Appliances
The technician needs to document whether the combustion appliance venting system shows evidence of a lack of maintenance or wear problems that could cause performance problems such as:
Blockages
Soot,
Corrosion, rust, or oxidation,
Improper support, slope, and/or termination
Insufficient draft.

## Slide 35: Atmospherically Vented Appliances
The technician needs to document whether the combustion appliance venting system shows evidence of a lack of maintenance or wear problems that could cause performance problems such as:
Blockages
Soot,
Corrosion, rust, or oxidation,
Improper support, slope, and/or termination
Insufficient draft.

## Slide 36: Atmospherically Vented Appliances
Improper support, slope, and/or termination

## Slide 37: Atmospherically Vented Appliances
Improper support, slope, and/or termination

## Slide 38: Atmospherically Vented Appliances
Additionally, the technician needs to perform a draft test (this is often done during the depressurization test). Draft tests need to be performed in accordance with the §11.6 in the NFGC (for gas-fired appliances) or §6.3 in the NFPA 31 (for oil-fired appliances), and record the findings for all of the previous requirements, NFGC and NFPA requirements must also be verified.

## Slide 39: Atmospherically Vented Appliances
NFGC §11.6 states that all draft hood appliances should be checked after 5 minutes of main burner operating time to make sure there is no draft hood spillage.
NFPA 31 §6.3 requires the chimney to be capable of providing the draft required by the equipment manufacturer. Additionally, when there are two or more oil appliances sufficient draft for both must be available. Finally, when there is a draft fan installed there must be an interlock switch to shut down the oil burner when the fan fails.

## Slide 40: Acceptable Documentation
Written or recorded records of CO measurements that were required on for the home and a note that combustion drafting was working properly during the back draft test shall be kept in the job file. Additional records for a failed Back draft test include:
Evidence or written notification of a fail test
Evidence of homeowner notification
Evidence of repair work done before Home performance improvements were implemented
(Note: this can be based on a test at a later date that provides proof that the CO level problems have been addressed)

## Slide 41: Insulation Introduction

## Slide 42: Insulation
Appendix 2 in: Technician’s Guide & Workbook for Home Performance Improvement is based on an ACCA Technical Bulletin: Determining Insulation Values In Existing Home

## Slide 43: Insulation

## Slide 44
Insulation Problem Areas

## Slide 45: DOE Climate Zones

## Slide 46: ASHRAE 90.2 (2007)
Ceilings | Zone 1 | Zone 2 | Zone 3 A B &C | Zone 4 | Zone 5 | Zone 6 | Zone 7 | Zone 8
Attic Space (Cavity) | 30 | 30 | 30 | 38 | 43 | 49 | 49 | 52
Without Attic Space (Cavity) | 13 | 22 | 22 | 22 | 26 | 38 | 38 | 38
Walls |  |  |  |  |  |  |  | 
Above Grade frame (Cavity) | 13 | 15 | 15 | 15 | 21 | 21 | 21 | 21
Frame Adjacent to unconditioned Space (Cavity) | 0 | 0 | 11 | 13 | 13 | 15 | 15 | 15
Above Grade Mass (Exterior) | 0 | 0 | 0 | 3 | 3 | 6 | 6 | 6
Above Grade Mass (Interior) | 0 | 0 | 4 | 4 | 4 | 15 | 15 | 21
Unvented Crawl Space (Interior) | 0 | 0 | 13 | 21 | 30 | 30 | 30 | 30
Floors |  |  |  |  |  |  |  | 
Slab on Grade (Perimeter) | NR | NR | NR | NR | NR | NR | NR | NR
Frame Over Exterior (Cavity) | 13 | 13 | 19 | 19 | 25 | 25 | 30 | 30
Frame Over Unconditioned Space Vented Crawlspace (cavity) | 13 | 13 | 19 | 19 | 25 | 25 | 30 | 30

## Slide 47: ASHRAE 90.2 (2007)
Ceilings | Zone 1 | Zone 2 | Zone 3 A B &C | Zone 4 | Zone 5 | Zone 6 | Zone 7 | Zone 8
Attic Space (Cavity) | 30 | 30 | 30 | 38 | 43 | 49 | 49 | 52
Without Attic Space (Cavity) | 13 | 22 | 22 | 22 | 26 | 38 | 38 | 38
Walls |  |  |  |  |  |  |  | 
Above Grade frame (Cavity) | 13 | 15 | 15 | 15 | 21 | 21 | 21 | 21
Frame Adjacent to unconditioned Space (Cavity) | 0 | 0 | 11 | 13 | 13 | 15 | 15 | 15
Above Grade Mass (Exterior) | 0 | 0 | 0 | 3 | 3 | 6 | 6 | 6
Above Grade Mass (Interior) | 0 | 0 | 4 | 4 | 4 | 15 | 15 | 21
Unvented Crawl Space (Interior) | 0 | 0 | 13 | 21 | 30 | 30 | 30 | 30
Floors |  |  |  |  |  |  |  | 
Slab on Grade (Perimeter) | NR | NR | NR | NR | NR | NR | NR | NR
Frame Over Exterior (Cavity) | 13 | 13 | 19 | 19 | 25 | 25 | 30 | 30
Frame Over Unconditioned Space Vented Crawlspace (cavity) | 13 | 13 | 19 | 19 | 25 | 25 | 30 | 30

## Slide 48: ASHRAE 90.2 (2007)
Ceilings | Zone 1 | Zone 2 | Zone 3 A B &C | Zone 4 | Zone 5 | Zone 6 | Zone 7 | Zone 8
Attic Space (Cavity) | 30 | 30 | 30 | 38 | 43 | 49 | 49 | 52
Without Attic Space (Cavity) | 13 | 22 | 22 | 22 | 26 | 38 | 38 | 38
Walls |  |  |  |  |  |  |  | 
Above Grade frame (Cavity) | 13 | 15 | 15 | 15 | 21 | 21 | 21 | 21
Frame Adjacent to unconditioned Space (Cavity) | 0 | 0 | 11 | 13 | 13 | 15 | 15 | 15
Above Grade Mass (Exterior) | 0 | 0 | 0 | 3 | 3 | 6 | 6 | 6
Above Grade Mass (Interior) | 0 | 0 | 4 | 4 | 4 | 15 | 15 | 21
Unvented Crawl Space (Interior) | 0 | 0 | 13 | 21 | 30 | 30 | 30 | 30
Floors |  |  |  |  |  |  |  | 
Slab on Grade (Perimeter) | NR | NR | NR | NR | NR | NR | NR | NR
Frame Over Exterior (Cavity) | 13 | 13 | 19 | 19 | 25 | 25 | 30 | 30
Frame Over Unconditioned Space Vented Crawlspace (cavity) | 13 | 13 | 19 | 19 | 25 | 25 | 30 | 30

## Slide 49: RESNET Insulation Grades
Grade I is the highest grade and: A Grade I rating can only be achieved on new work upon the completion of an installation inspection process and must meet all of these additional requirements:
Installed according to insulation manufacturer’s instructions:
  Fills each cavity side-to side and top to bottom.
  No substantial gaps or voids around obstructions.
  Split or fitted tightly around wiring and other services.

## Slide 50: RESNET Insulation Grades
No exterior sheathing is visible through gaps in the material.
Minimal Compression.
Additionally, there is one allowance for a less than perfect insulation installation: incomplete fill or compression of up to 30% of intended thickness, to up to 2% of the area.

## Slide 51: RESNET Insulation Grades
Grade II: Most of the insulation that has traditionally been well installed will fall into a Grade II rating. Grade II ratings can only be achieved on new work upon the completion of an installation inspection process and must meet all of these additional requirements:
Moderate to frequent defects:
  Gaps around wiring, electrical outlets, plumbing, other intrusions
  Rounded edges or “Shoulders”

## Slide 52: RESNET Insulation Grades
Gaps/spaces clear through the insulation amounting to up to 2% of the total surface area covered by the insulation; or incomplete fill or compression of up to 30% of intended thickness, up to 10% of the area

## Slide 53: RESNET Insulation Grades
Grade III: Technician’s will often find Grade III insulation. From a home performance perspective this rating will offer the best potential for improving energy efficiency through an upgrade. As with Grade II, the ratings can only be achieved on new work upon the completion of an installation inspection process and must meet all of these additional requirements:
Gaps and voids to greater than 2% of the surface area the insulation occupies but less than 5%

## Slide 54: Insulation Grade Area Calculation

## Slide 55: Insulation Grade Area Calculation
Formula for calculating the percentage area: Anomaly Area ÷ Total Area × 100 = % area
An insulation grade value is calculated using area data from a thermal image scan done in a home with 3,100 square feet of inspected surfaces. The image showed 50 square feet of anomalies so using the formula:
Anomaly Area ÷ Total Area × 100 = % area;
50 ÷ 3,100 × 100 = % area = 1.61%

## Slide 56: Insulation Grade Area Calculation
Formula for calculating the percentage area: Anomaly Area ÷ Total Area × 100 = % area
An insulation grade value is calculated using area data from a thermal image scan done in a home with 3,100 square feet of inspected surfaces. The image showed 50 square feet of anomalies so using the formula:
Anomaly Area ÷ Total Area × 100 = % area;
50 ÷ 3,100 × 100 = % area = 1.61%

## Slide 57: Acceptable Documentation
Written or recorded records (e.g., photo) of insulation measurements including insulation thickness and area used for calculations involving insulation upgrade and/or repair proposals.