## Slide 1: Duct Design Basics Lesson 4 Manual D Primer

## Slide 2: Duct Sizing 4.3

## Slide 3
Duct Sketch/Drawing
1
2
3
4
5
6
7
8
9
10
11
12
13
1
2
3
4

## Slide 4
Duct Sketch/Drawing
1
2
3
4
5
6
7
8
9
10
11
12
13
1
2
3
4
1N EL 15
2P 5 or more EL 75
4K EL 30
2P EL 35
9O EL 15
9P EL 70
1
2
3
Galvanized Round Duct
Flex Round Duct

## Slide 5
Duct Sketch/Drawing
1
2
3
4
5
6
7
8
9
10
11
12
13
1
2
3
4
1N EL 15
2P 5 or more EL 75
4K EL 30
2P EL 35
9O EL 15
9P EL 70
1
2
3
Galvanized Round Duct
Flex Round Duct

## Slide 6
Fittings: Galvanized Duct in ft:
1N EL 15 1 3 ft.
9P EL 70 2 40 ft.
2P EL 75 3 7 ft.
9O EL 15 Total 50 ft.
4K EL 30 Flex Duct in ft.
Total 205 Ft. 1 10 ft.
Total 50 + 10 + 205 = 265 ft.
Supply Duct Size Calculation

## Slide 7
Duct Sketch/Drawing
1
2
3
4
5
6
7
8
9
10
11
12
13
1
2
3
4
1N EL 15
2P 5 or more EL 75
4K EL 30
2P EL 35
9O EL 15
9P EL 70
1
2
3
Galvanized Round Duct

## Slide 8
Supply Duct Size Calculation
Fittings: Galvanized Duct in ft:
1N EL 15 1 3 ft.
9P EL 70 2 50 ft.
2P EL 75 3 16 ft.
9O EL 15 Total 69 ft.
4K EL 30
Total 205 Ft.
Total 69 + 205 = 274 ft.

## Slide 9
Return Duct Size Calculation
1
2
3
4
5
6
7
8
9
10
11
12
13
1
2
3
4
4Y EL 30
Flex Round Duct Return
1
2
Junction Box
10 G EL 75

## Slide 10
Fittings: Flex Duct in ft.
4Y EL 30 1 4 ft.
10 G EL 75 2 6 ft.
Total 105 ft Total 10 ft.
Total 105 + 10 = 115 ft.
Return Duct Size Calculation

## Slide 11
Return Duct Size Calculation
1
2
3
4
5
6
7
8
9
10
11
12
13
1
2
3
4
4Y EL 30
Flex Round Duct Return
1
2
Junction Box
10 G EL 75

## Slide 12
Fittings: Flex Duct in ft.
4Y EL 30 1 4 ft.
10 G EL 75 2 12 ft.
Total 105 ft. Total 16 ft.
Total 105 + 16 = 121 ft.
Return Duct Size Calculation

## Slide 13
Return plus Supply = 121 + 274 = 395 ft
Return plus Supply = 115 + 265 = 380 ft
Return Plus Supply Duct Size Calculation

## Slide 14
Pressure Drop for Airside Components
Only duct has been shown thus far!
Anything placed in the duct that is not included in
The equipment manufacturer’s external static pressure (ESP)
rating needs to be included in the System friction loss total.
ESP

## Slide 15
Pressure Drop for Airside Components
Only duct has been shown thus far!
Anything placed in the duct that is not included in
The equipment manufacturer’s external static pressure (ESP)
rating needs to be included in the System friction loss total.
Filters
Coils
Diffusers & Grilles
Heating Elements
Humidifier
Balancing damper

## Slide 16
Pressure Drop for Airside Components
Only duct has been shown thus far!
Anything placed in the duct that is not included in
The equipment manufacturer’s external static pressure (ESP)
rating needs to be included in the System friction loss total.
Filters
Coils
Diffusers & Grilles
Heating Elements
Humidifier
Balancing damper
ESP = 0.50

## Slide 17
Pressure Drop for Airside Components
SP = 0.055

## Slide 18
Pressure Drop for Airside Components
SP = 0.010
0.010 + 0.055 = .065

## Slide 19
Available Static Pressure (ASP)
Step 1: Manufacturer’s blower data
XYZ Brand ESP 0.50 @ 1,200 CFM (wet coil, filter included)
Step 2: Calculate Component Losses
Filters--------------------------- N/A
Coils----------------------------- N/A
Diffusers & Grilles----------- 0.065
Heating Elements------------ 0.02
Humidifier--------------------- 0.03
Balancing damper----------- N/A (Bad Idea)
Total--------------------------------- 0.115 IWC

## Slide 20
Available Static Pressure (ASP)
Step 3: Available Static Pressure (ASP)
ASP = ESP – CPL = 0.50 – 0.115 = 0.385 IWC
Step 4: Total Effective Length (TEL)
Supply Duct TEL + Return TEL = 121 + 274 = 395 Feet
Step 5: Friction Rate Design Value
FR = ASP x 100 ÷ TEL = 0.385 x 100 ÷ 395 = 0.098 IWC/100

## Slide 21
Available Static Pressure (ASP)
Step 3: Available Static Pressure (ASP)
ASP = ESP – CPL = 0.50 – 0.115 = 0.385 IWC
Step 4: Total Effective Length (TEL)
Supply Duct TEL + Return TEL = 121 + 274 = 395 Feet
Step 5: Friction Rate Design Value
FR = ASP x 100 ÷ TEL = 0.385 x 100 ÷ 395 = 0.098 IWC/100
0.101 – 0.098 = 0.003 Difference
FR = ASP x 100 ÷ TEL = 0.385 x 100 ÷ 380 = 0.101 IWC/100

## Slide 22
Duct Size Calculation BTU & CFM

## Slide 23
Duct Size Calculation BTU & CFM
1,629
485
Bedroom 1
43.75

## Slide 24
Duct Size Calculation BTU & CFM
Bedroom 1
2,253
230
400
1,630
400

## Slide 25
Run-Trunk | Heat BTUH | Cool BTUH | Heat CFM | Cool CFM | DSN CFM | Round Dia. | VEL FPM | Final Dia.
1 | 8,320 | 5,600 | 260 | 200 | 260 | 9 | 600 | 9
2 | 2,144 | 1,680 | 67 | 60 | 67 | 6 | 411 | 6
3 | 640 | 560 | 20 | 20 | 20 | 3 | N/A | 3
4 | 2,560 | 2,548 | 80 | 91 | 91 | 6 | 462 | 6
5 | 2,560 | 2,548 | 80 | 91 | 91 | 6 | 462 | 6
6 | 1,280 | 1,260 | 40 | 45 | 45 | 5 | 340 | 5
7 | 2,560 | 2,912 | 80 | 104 | 104 | 6 | 540 | 6
8 | 2,496 | 2,800 | 78 | 100 | 100 | 6 | 522 | 6
9 | 2,496 | 2,800 | 78 | 100 | 100 | 6 | 522 | 6
10 | 2,944 | 1,680 | 92 | 60 | 92 | 6 | 465 | 6
11 | 2,912 | 1,652 | 91 | 59 | 91 | 6 | 463 | 6
12 | 2,176 | 1,400 | 68 | 50 | 68 | 6 | 410 | 6
13 | 2,272 | 1,736 | 71 | 62 | 71 | 5 | 513 | 5
 |  | Trunk 1 | 420 | 382 | 442 | 12 | 560 | 12
 |  | Trunk 2 | 685 | 660 | 758 | 14 | 720 | 14
Supply Trunk Considerations for Noise
Conservative = 700 FPM
Maximum = 900 FPM

## Slide 26
Run-Trunk | Heat BTUH | Cool BTUH | Heat CFM | Cool CFM | DSN CFM | Round Dia. | VEL FPM | Final Dia.
1 | 8,320 | 5,600 | 260 | 200 | 260 | 9 | 600 | 9
2 | 2,144 | 1,680 | 67 | 60 | 67 | 6 | 411 | 6
3 | 640 | 560 | 20 | 20 | 20 | 3 | N/A | 3
4 | 2,560 | 2,548 | 80 | 91 | 91 | 6 | 462 | 6
5 | 2,560 | 2,548 | 80 | 91 | 91 | 6 | 462 | 6
6 | 1,280 | 1,260 | 40 | 45 | 45 | 5 | 340 | 5
7 | 2,560 | 2,912 | 80 | 104 | 104 | 6 | 540 | 6
8 | 2,496 | 2,800 | 78 | 100 | 100 | 6 | 522 | 6
9 | 2,496 | 2,800 | 78 | 100 | 100 | 6 | 522 | 6
10 | 2,944 | 1,680 | 92 | 60 | 92 | 6 | 465 | 6
11 | 2,912 | 1,652 | 91 | 59 | 91 | 6 | 463 | 6
12 | 2,176 | 1,400 | 68 | 50 | 68 | 6 | 410 | 6
13 | 2,272 | 1,736 | 71 | 62 | 71 | 5 | 513 | 5
 |  | Trunk 1 | 420 | 382 | 442 | 12 | 560 | 12
 |  | Trunk 2 | 685 | 660 | 758 | 14 | 720 | 14

## Slide 27
Run-Trunk | Heat BTUH | Cool BTUH | Heat CFM | Cool CFM | DSN CFM | Round Dia. | VEL FPM | Final Dia.
1 | 8,320 | 5,600 | 260 | 200 | 260 | 9 | 600 | 9
2 | 2,144 | 1,680 | 67 | 60 | 67 | 6 | 411 | 6
3 | 640 | 560 | 20 | 20 | 20 | 3 | N/A | 3
4 | 2,560 | 2,548 | 80 | 91 | 91 | 6 | 462 | 6
5 | 2,560 | 2,548 | 80 | 91 | 91 | 6 | 462 | 6
6 | 1,280 | 1,260 | 40 | 45 | 45 | 5 | 340 | 5
7 | 2,560 | 2,912 | 80 | 104 | 104 | 6 | 540 | 6
8 | 2,496 | 2,800 | 78 | 100 | 100 | 6 | 522 | 6
9 | 2,496 | 2,800 | 78 | 100 | 100 | 6 | 522 | 6
10 | 2,944 | 1,680 | 92 | 60 | 92 | 6 | 465 | 6
11 | 2,912 | 1,652 | 91 | 59 | 91 | 6 | 463 | 6
12 | 2,176 | 1,400 | 68 | 50 | 68 | 6 | 410 | 6
13 | 2,272 | 1,736 | 71 | 62 | 71 | 5 | 513 | 5
 |  | Trunk 1 | 420 | 382 | 442 | 12 | 560 | 12
 |  | Trunk 2 | 685 | 660 | 758 | 12 | 720 | 14

## Slide 28
Duct Sketch/Drawing
260 CFM
67 CFM
284 CFM
45 CFM
91 CFM each
104 CFM
104 CFM
182 CFM
612 CFM
20 CFM
71 CFM
68 CFM
91 CFM
92 CFM
100 CFM each
1
2
3
4
5
6
8
7
9
10
11
12
1
2
3
13
4
9
12
6
6
Trunk 1

## Slide 29
260 CFM
67 CFM
284 CFM
45 CFM
91 CFM each
104 CFM
104 CFM
182 CFM
612 CFM
20 CFM
71 CFM
68 CFM
91 CFM
92 CFM
100 CFM each
1
2
3
4
5
6
8
7
9
10
11
12
1
2
3
13
4
9
12
6
6
Trunk 1
Do the same for the other supply trunk and the 4
returns!

## Slide 30
260 CFM
67 CFM
284 CFM
45 CFM
91 CFM each
104 CFM
104 CFM
182 CFM
612 CFM
20 CFM
71 CFM
68 CFM
91 CFM
92 CFM
100 CFM each
1
2
3
4
5
6
8
7
9
10
11
12
1
2
3
13
4
9
12
6
6
Trunk 1
Do the same for the other supply trunk and the 4
returns!
6
5
6
6
6
8
7
7
5
3
Trunk 2
6
14

## Slide 31
260 CFM
67 CFM
284 CFM
45 CFM
91 CFM each
104 CFM
104 CFM
182 CFM
612 CFM
20 CFM
71 CFM
68 CFM
91 CFM
92 CFM
100 CFM each
1
2
3
4
5
6
8
7
9
10
11
12
1
2
3
13
4
This will never be a QI Job until Balancing dampers
are added so it can be balanced.
7
9
13
19
10

## Slide 32
260 CFM
67 CFM
284 CFM
45 CFM
91 CFM each
104 CFM
104 CFM
182 CFM
612 CFM
20 CFM
71 CFM
68 CFM
91 CFM
92 CFM
100 CFM each
1
2
3
4
5
6
8
7
9
10
11
12
1
2
3
13
4
This will never be a QI Job until Balancing dampers
are added so it can be balanced.
7
9
13
19
10