## Slide 1: Duct Design Basics Lesson 4 The Manual D Primer

## Slide 2: Fitting Equivalent Length 4.5

## Slide 5
What happens when we have a different reference velocity?
For example what would the EL be for the 1C fitting
If we were designing a system to operate at 600 FPM?

## Slide 6
Formula:
ELFor Fitting = ELTable Value x [VFor Fitting ÷ VTable Value]2

## Slide 8
Formula:
ELFor Fitting = ELTable Value x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 35 x [600 ÷ 900]2 = 15.56

## Slide 9
Formula:
ELFor Fitting = ELTable Value x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 35 x [600 ÷ 900]2 = 15.56
0.444444….

## Slide 10
What happens when we have a different reference friction rate?
For example what would the EL be for the 1C fitting
If we were designing a system to operate at a FR of 0.06?

## Slide 11
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting]
ELFor Fitting = 35 x [0.08 ÷ 0.06] = 46.67

## Slide 12
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting]
ELFor Fitting = 35 x [0.08 ÷ 0.06] = 46.67
1.3333….

## Slide 13
What happens when we have a different reference friction rate and a different Velocity?

## Slide 14
What happens when we have a different reference friction rate and a different Velocity?
For example what would the EL be for the 1C fitting
If we were designing a system to operate at a FR of 0.06 and a velocity of 600 FPM?

## Slide 15
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2

## Slide 16
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 35 x [0.08 ÷ 0.06] x [600 ÷ 900]2 = 20.74

## Slide 17
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 35 x [0.08 ÷ 0.06] x [600 ÷ 900]2 = 20.74
0.59

## Slide 19
What would the EL be if we have a design for 500 FPM at 0.08 IWC?

## Slide 20
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [0.08 ÷ 0.08] x [600 ÷ 700]2 = 55.1

## Slide 21
What would the EL be if we have a design for 700 FPM at 0.06 IWC?

## Slide 22
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [0.08 ÷ 0.06] x [700 ÷ 700]2 = 100

## Slide 23
What would the EL be if we have a design for 500 FPM at 0.07 IWC?

## Slide 24
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2

## Slide 25
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [0.08 ÷ 0.06] x [600 ÷ 700]2 = 74

## Slide 26
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [0.08 ÷ 0.06] = 100
ELFor Fitting = 75 x [0.08 ÷ 0.10] = 60

## Slide 27
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [0.08 ÷ 0.06] = 100
ELFor Fitting = 75 x [0.08 ÷ 0.10] = 60
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [600 ÷ 700] = 64.29
ELFor Fitting = 75 x [900 ÷ 700] = 96.42

## Slide 28
Formula:
ELFor Fitting = ELTable Value x [FRTable Value÷ FRFor Fitting] x [VFor Fitting ÷ VTable Value]2
ELFor Fitting = 75 x [0.08 ÷ 0.06] x [600 ÷ 700]2 = 74

## Slide 29
For Math Lovers:
A formula based on equal friction rates for the conversion from rectangular ducts to a circular equivalent.
Round Duct Diameter (In) = 1.3 x [(a x b)0.625) ÷ (a + b)0.25]
Where a = length of side one in inches and b = length of side 2 in inches
a
b
Side 1
Side 2

## Slide 30
For Math Lovers:
A formula based on equal friction rates for the conversion from rectangular ducts to a circular equivalent.
Round Duct Diameter (In) = 1.3 x [(a x b)0.625) ÷ (a + b)0.25]
Where a = length of side one in inches and b = length of side 2 in inches
a
b
Side 1
Side 2
See Appendix 2 in Manual D for Conversion Charts
and Formulas or use the ACCA Duct Slide Rule!

## Slide 31
For Math Lovers:
A formula based on equal friction rates for the conversion from rectangular ducts to a circular equivalent.
Round Duct Diameter (In) = 1.3 x [(a x b)0.625) ÷ (a + b)0.25]
Where a = length of side one in inches and b = length of side 2 in inches
a
b
Side 1
Side 2
See Appendix 2 in Manual D for Conversion Charts
and Formulas or use the ACCA Duct Slide Rule!