## Slide 1: Part 1 Technician’s Guide & Workbook for Duct Diagnostics and Repair

## Slide 2: Technician’s Guide & Workbook for Duct Diagnostics and Repair

## Slide 3: Section 1.1 Duct Basics: Energy Losses

## Slide 4: Proven Design Practices
TOTAL CFM = 1267
Furnace
Return Air
Supply
Air

## Slide 5: Proven Design Practices
TOTAL CFM = 1267
Return Grille Inlets

## Slide 6: Proven Design Practices
TOTAL CFM = 1267
Supply Register Outlets

## Slide 7: Proven Design & Installation Practices
Meeting the duct leakage testing requirements in
the ANSI/ACCA 5-2015 HVAC Quality Installation
Specification will provide energy savings over
traditional duct Installation practices.
Available for free downloading at: www.acca.org/quality

## Slide 8: Proven Design & Repair Practices
Upgrading to the latest local insulation levels.
Repairing and seal damaged insulation.
ENERGY STAR™ Cost Effective Duct Insulation R-Values* |  |  | 
 |  | Unheated /unconditioned Attic*** | Unheated /unconditioned Basement/ Crawlspace***
If you live in a climate that is: | System Type** |  | 
Warm with cooling and minimal heating requirements (i.e. FL & HI; costal CA; southeast TX; southern LA, AR, MS, AL & GA) | Gas/oil or heat pump | R4 to R8 | None to R-4
 | Electric resistance | R4 to R8 | None to R-4
Mixed with moderate heating and cooling requirements (i.e., VA, WV, KY, MO, NE, OK, OR, WA, & ID; southern IN, KS, NM,7 AZ; northern LA, AR, MS, AL, & GA; inland CA & western NV.) | Gas/oil or heat pump | R4 to R8 | R2 to R8
 | Electric resistance | R4 to R8 | R2 to R8
Cold [ie., PA, NY, New England, northern Midwest, Great Lakes area, mountainous area (e.g., CO, WY, UT, etc.)] | Gas/oil | R6 to R11 | R2 to R11
 | Heat pump or electric resistance | R6 to R11 | R2 to R11
* Adapted from Modera et al., “Impacts of Residential Duct Insulation on HVAC Energy Use and Life Cycle Cost to Consumers,” ASHRAE Transactions (#AT-96-13-4). ** Insulation is also effective at reducing cooling bills. *** Updated to 2015 values |  |  | 

## Slide 9
U.S. Department of Energy Duct Insulation and Sealing Requirements in Commercial Buildings* |  |  |  |  |  |  | 
Duct Locations |  |  |  |  |  |  | 
Climate Zone | Exterior | Vented Attic | Unvented Attic above Insulated Ceiling | Unvented Attic with Roof Insulation** | Unconditioned Space*** | Indirectly Conditioned Space**** | Buried
Supply Ducts |  |  |  |  |  |  | 
1 | R-6 | R-6 | R-8 | R-3.5 | R-3.5 | none | R-3.5
2 | R-6 | R-6 | R-6 | R-3.5 | R-3.5 | none | R-3.5
3 | R-6 | R-6 | R-6 | R-3.5 | R-3.5 | none | R-3.5
4 | R-6 | R-6 | R-6 | R-3.5 | R-3.5 | none | R-3.5
5 | R-6 | R-6 | R-6 | R-1.9 | R-3.5 | none | R-3.5
6 | R-8 | R-6 | R-6 | R-1.9 | R-3.5 | none | R-3.5
7 | R-8 | R-6 | R-6 | R-1.9 | R-3.5 | none | R-3.5
8 | R-8 | R-8 | R-8 | R-1.9 | R-6 | none | R-6
Return Ducts |  |  |  |  |  |  | 
1 to 8 | R-3.5 | R-3.5 | R-3.5 | none | none | none | none
* https://www.energycodes.gov/sites/default/files/documents/cn_commercial_duct_insulation_sealing.pdf ** Insulation R-Values, measured in (h-ft2 OF) ÷ BTU, are for insulation as installed and do not include film resistance. The required minimum thicknesses do not consider water vapor transmission and possible surface condensation. Where exterior walls are used as plenum walls, wall insulation shall be as required by the most restrictive condition of Section 6.4.4.2 or Section 5. Insulation resistance measured on a horizontal plane in accordance with ASTM C518 at a mean temperature of 75OF at the installed thickness. *** Includes Crawl Spaces ****Includes return air plenums with or without exposed roofs above. |  |  |  |  |  |  | 

## Slide 10: 2015 International Energy Conservation Code Residential Insulation
Residential prescriptive section (R403.3.1) calls for:
a minimum of R-8 insulation for supply and return
ducts with a diameter is greater than 3” and a R-6
insulation for ducts smaller than 3”. It also requires
supply and return ducts in other building areas
above 3” in diameter to be insulated to the R-6 level
and those below 3” to an R-4.2 level. Existing duct
systems were installed to meet various outdated
code requirements.

## Slide 11: 2015 International Energy Conservation Code Commercial Insulation
Commercial section C403.2.9, the requirement for
supply and return ducting in unconditioned space is;
it must have an insulation value of R-6 unless they
are in climate zones 1 through 4 where R-8 is required
or zones 5 through 8 where a value of R-12 is
required; plus all duct in a building envelope
assembly must be separated from the building
exterior or unconditioned spaces by a minimum of
R-8 insulation for zones 1 through 4 and R-12 in
zones 5 through 8.

## Slide 12: Department of Energy (DOE) Climate Zones

## Slide 13: Energy Losses & Costs
Repairs to leaking or poorly insulated duct may
result in a 50% reduction in energy loss!
Based on a national average of $0.92 per therm
(100,000 Btu natural gas) and $0.11 cents per
Kilowatt-hour electrical cost, a typical home would
save $2,000.00 per year in utility costs.
Payback for insulation repairs often less than a year!

## Slide 14: Energy Losses & Costs
Ducts loose energy in one of two ways:
Conduction of heat through the duct wall
And
Leaks through holes, cracks and seems.
Note: in cooling mode condensation may
damage insulation that is not properly sealed

## Slide 15: Conduction
Heat Leaving The Duct Surface
During Heating Season

## Slide 16: Conduction
Heat Entering The Duct Surface
During Cooling Season

## Slide 17: Conduction

## Slide 18: Conduction

## Slide 19: Leaks
Hole
Seams

## Slide 20: Duct Sealed
NO LEAKS

## Slide 21: Totally Sealed Duct System

## Slide 22: Leaking Return Duct

## Slide 23: Leaking Supply Duct

## Slide 24: Lessons Learned
You should now be able to explain why fixing leaks in duct systems should be recommended.
You should now be able to recommend insulation values for duct repairs.
You should now be able to explain where outside air leaks in for supply and return duct leaks (based on the duct location).