## Slide 1: Part 12 Technician’s Guide & Workbook for Duct Diagnostics and Repair

## Slide 2: Section 5.1: Health & Safety Issues

## Slide 3: Health
Poorly designed or improperly installed duct
systems can compromise health and safety.
The distinction between health and safety can
be a fine one.

## Slide 4: Health
Generally, when a condition existing over a long
period of time impairs the well-being of the
occupants, but is not an immediate threat to life,
it is referred to as a health problem.

## Slide 5: Health and Safety Issue
Toxins and termiticides from the ground:
Concern:
Radon and other toxic gases are pulled into a depressurized basement or crawl space, then into return ducts and distributed to rooms.
Corrective Action:
1) Radon mitigation (if warranted).
2) Relieve basement depressurization.
3) Seal return ducts.

## Slide 6: Health and Safety Issue
Toxic Chemical in the ground

## Slide 7: Health and Safety Issue
Fumes from stored contaminants:
Concern:
Vapors from stored chemicals are sucked into return ducts, or released into conditioned areas from a pressurized basement (pressure causes vapors to leak into conditioned areas.)
Corrective Action:
1) Remove chemicals.
2) Seal return ducts.
3) Relieve basement pressurization (if severe). Sealing supply ducts should help here.

## Slide 8: Health and Safety Issue

## Slide 9: Health and Safety Issue
Auto exhaust fumes:
Concern:
Return ducts in garage suck in fumes from idling car and deliver to building.
Corrective Action:
1) Seal return ducts.
2) Post warning sign.
3) Warn / instruct occupants.

## Slide 10: Health and Safety Issue

## Slide 11: Health and Safety Issue
Biological Growth:
Concern:
Excessive humidity promotes the development of molds and organisms causing wood rot.
Corrective Action:
1) Stop moisture at source (when possible).
2) Seal return ducts.
3) Check refrigerant charge on air conditioner 4) Downsize air conditioner.

## Slide 12: Health and Safety Issue

## Slide 13: Health and Safety Issue
Draft Spillage:
Concern:
Negative pressure in furnace room causes reverse flow in flue, spilling combustion products which are sucked into return ducts and distributed to living space.
Corrective Action:
1) Relieve depressurization of furnace room
2) Seal return ducts.
3) Install power-vented appliances.

## Slide 14: Health and Safety Issue

## Slide 15: Health and Safety Issue
Fireplace/Stove Back draft:
Concern:
Negative pressure in room with a fireplace or wood stove causes reverse flow down chimney, spilling carbon-monoxide laden combustion products directly into the living space.
Corrective Action:
1) Relieve depressurization of fireplace room.
2) Supply outside air to fireplace or stove.

## Slide 16: Health and Safety Issue

## Slide 17: Health and Safety Issue
Flame Rollout:
Concern:
Strongly negative pressure in furnace room causes sufficient reverse flow to blow fuel/air mixture from appliances into rooms, where it poses a fire hazard upon ignition.
Corrective Action:
1) Relieve depressurization of furnace room.
2) Install power-vented appliances.

## Slide 18: Health and Safety Issue
Furnace
Roll Out

## Slide 19: Health and Safety Issue
Lack of air change in occupied space:
Concern:
All of the dust, fumes, combustion byproducts, and other volatile organic compounds (VOC) can build up in the air causing occupant illness especially the young, elderly and those with immune deficiencies.
Corrective Action:
1) Install ASHRAE 62.2 compliant make up/ outside air capability (see Appendix 4).

## Slide 20: Health and Safety Issue
ASHRAE 62.2: Appendix 4 in the Technician’s Guide & Workbook for Duct Diagnostics and Repair
Ventilation Air Requirements in CFM |  |  |  |  | 
Floor Area ft2 | Number of Bedrooms |  |  |  | 
 | 1 | 2 | 3 | 4 | 5
Less Than 500 | 30 | 38 | 45 | 53 | 60
501-1000 | 45 | 53 | 60 | 68 | 75
1001-1500 | 60 | 68 | 75 | 83 | 90
1501-2000 | 75 | 83 | 90 | 98 | 105
2001-2500 | 90 | 98 | 105 | 113 | 120
2501-3000 | 105 | 113 | 120 | 128 | 135
3001-3500 | 120 | 128 | 135 | 143 | 150
3501-4000 | 135 | 143 | 150 | 158 | 165
4001-4500 | 150 | 158 | 165 | 173 | 180
4501-5000 | 165 | 173 | 180 | 188 | 195

## Slide 21: Lessons Learned
You should now be able to recognize types of health and safety related issues.
You should now be able to recognize dangerous/hazardous conditions for combustion appliance operation.
You should now be able to find the ASHRAE minimum make up air requirement for a home.