## Slide 1: Part 16 Technician’s Guide & Workbook for Duct Diagnostics and Repair

## Slide 2: Section 6.1: Customer Opportunities

## Slide 3: Existing Duct Systems

## Slide 4: Duct Efficiency
When the system is operating, duct systems lose energy in two main ways:
1. Conduction of heat through duct walls; and
2. Leakage of air through holes and joints in the duct system.
      Air in from unconditioned spaces through return leakage.
      Air out to unconditioned spaces through supply duct leakage.

## Slide 5: Thermal Comfort
Inadequate cooling capacity
Poor Humidity Control
Rooms Hot and/or Cold
Drafty Areas

## Slide 6: System Repairs

## Slide 7: Health and Safety
Golden Opportunity Number 1:
Comfort, Safety, and Health Enhancements
When ducts are repaired, any improvement in
thermal comfort will be noticed immediately.
The main comfort improvement in duct repairs stems from improved delivery (and return pathways) of conditioned air, especially to rooms that are at the end of long duct runs.

## Slide 8: Health and Safety
Golden Opportunity Number 2:
Improving Heat Pump Efficiency
Sealing and insulating ducts reduces the load the heat pump must meet at any given outdoor temperature. As a result, the heat pump compressor can handle the total load lower outdoor temperatures than before. This can result in an overall improvement in system efficiency that is up to 50% higher than what one would expect when only considering the ducts losses.

## Slide 9: Health and Safety
Insulating supply ducts raises the delivered air temperature in the heating mode. That is often a significant comfort benefit for heat pump systems because of the perceptions of draftiness caused by the lower supply air temperatures. Due to the higher cost of operating in the all-electric backup heat mode, duct efficiency provides an added bang for the buck in heat pump systems.

## Slide 10: Health and Safety
Golden Opportunity Number 3:
Attic Ducts especially in Hot Humid Climates
In a worst-case scenario, the HVAC system may not be able to meet the load operating at 100%. Unfortunately, customer complaints that the air conditioning system is not providing adequate cooling have too often been dealt with by installing a larger unit.

## Slide 11: Health and Safety
Golden Opportunity Number 4:
Duct Repair During Equipment Replacement
Benefits to the customer:
Upgraded equipment efficiency, with lower fuel costs;
Better duct performance, with lower fuel costs and improved thermal comfort; and
Potential to reduce the size and cost of the replacement equipment

## Slide 12: Health and Safety
For example, suppose a 3-ton air conditioner has failed. Should the unit simply be swapped out, or should a duct repair be considered? In order to arrive at a proposal that is in the customer’s best interest, the contractor should know the following:
What will the customer’s cost be for a duct repair job, and how will this compare with the annual energy savings?

## Slide 13: Health and Safety
Will the duct repair allow a smaller unit to be used, and how much of a first-cost saving will this provide?
Should the new unit have the minimum efficiency permitted according to the national standards, or should a more efficient one be chosen?

## Slide 14
For one example job, it was determined that if the ducts were repaired, a 2-ton unit would be adequate, whereas if they were not repaired, a 3-ton replacement unit would be required. The contractor priced his services as follows:
A proposed duct repair package was priced at $900;
A 2-ton unit would be $500 less than the comparable 3-ton unit; and
Fixing the ducts would save approximately $200 per year in operating costs.

## Slide 15
This information permitted a quick calculation of a simple payback time for the duct repair. The net cost of the retrofit was $900 minus the $500 savings for the smaller equipment, or $400. Saving $200 annually would pay back the initial investment in two years.
The economics of duct repair are helped considerably by the savings on the smaller unit. If the equipment did not have to be replaced, the payback time would be $900 divided by $200 or 4.5 years.

## Slide 16: Opportunities for New Construction
In new construction, the details in the design of a duct system are still open to change. This presents an opportunity that is generally not present in existing buildings. The flip side of this, however, is that once this opportunity is squandered through a business as usual installation, it can never be regained. Research has shown that existing duct systems located in vented attics and open crawl spaces will typically lose 25% to 40% of the heating or cooling energy input to them by the equipment.

## Slide 17: Opportunities In New Buildings
In new construction, the details in the design of a duct system are still open to change. This presents an opportunity that is generally not present in existing buildings. The flip side of this, however, is that once this opportunity is squandered through a business as usual installation, it can never be regained. Research has shown that existing duct systems located in vented attics and open crawl spaces will typically lose 25% to 40% of the heating or cooling energy input to them by the equipment.

## Slide 18: Impediments In New Construction
At least five difficulties stand in the way of widespread practice of placing ducts in the conditioned-space:
Difficulty in hiding ductwork;
Perceived extra cost;
Need for building designers to become involved with the details of the duct design; and
Increased scheduling complications if other trades are needed on the job; and
Lost usable space.

## Slide 19: Good Design Practices
Good practice has the following 6 elements:
Design the total heating and cooling system and select the equipment using Manuals J, S, and D (residential) Manuals N,CS, and Q (commercial);
Minimize the surface area of ducts outside the conditioned space through good routing, use of low-loss fittings, and placement of registers near interior walls;
Specify suitably low levels of air leakage to/from the outside and include a post-installation leakage test in the construction plan. As a benchmark, it is suggested that air leakage to/from the outside should not exceed 5% of total airflow on either the supply or return side;

## Slide 20: Good Installation
See that ducts are sealed using materials and techniques that will last as long as the ducts. If the ducts are sealed by hand, UL Listed (not UL Classified) mastic should be used. Automated sealing may also be considered (See Section 2 in this Guide & Workbook);
Insulate ducts outside the conditioned space, at least to R-6 and preferably R-8 or R-11 depending on the local climate zone requirements; and
Make sure the ducts are tested for leakage and balanced in accordance with ANSI/ACCA 5 QI-2015 requirements.

## Slide 21: Lessons Learned
You should now be able to identify 3 golden opportunities for upselling an HVAC system installation to include duct repairs for the owners comfort and financial benefit.
You should now be able to name 6 opportunities for improving performance and efficiency in new construction designs and installations.
You should now be able to explain basic operating savings based on improving an existing duct system’s performance capabilities.