## Slide 1: Part 3 Technician’s Guide & Workbook for Duct Diagnostics and Repair

## Slide 2: Section 1.3 Duct Basics: System Efficiency Losses

## Slide 3: Filtration
Std 52.2 MERV | Average ASHRAE Dust Spot Efficiency Std 52.1 | Average ASHRAE Arrestance Std 52.1 | Particle Size Ranges | Typical Applications | Typical Filter Type
1-4 | <20% | 60 to 80% | > 10.0 µm | Residential / Minimum Light / Commercial Minimum / Equipment Protection | Permanent / Self Charging (passive) Washable / Metal, Foam / Synthetics Disposable Panels Fiberglass / Synthetics
5-8 | <20 to 35% | >80 to 95% | 3.0 - 10.0 µm | Industrial Workplaces Commercial Better / Residential/ Paint Booth / Finishing | Pleated Filters Extended Surface Filters Media Panel Filters
9-12 | 40 to 75% | >95 to 98% | 1.0 - 3.0 µm | Superior / Residential Better / Industrial Workplaces Better / Commercial Buildings | Non-Supported / Bag Rigid Box Rigid Cell / Cartridge
13-16 | 80 to 95% + | >98 to 99% | 0.30 - 1.0 µm | Smoke Removal General Surgery Hospitals & Health Care Superior / Commercial Buildings | Rigid Cell / Cartridge Rigid Box Non-Supported / Bag
17-201 | 99.972 99.992 99.9992 | N/A | ≤ 0.30 µm | Clean Rooms High Risk Surgery Hazardous Materials | HEPA ULPA

## Slide 4: Telltale Signs of Problem Ducts
Heat Leaving Duct Surface During Heating Season
Uninsulated Ducts

## Slide 5: Telltale Signs of Problem Ducts
Heat Entering Duct Surface During Cooling Season
Uninsulated Ducts

## Slide 6: Common Return

## Slide 7: Telltale Signs of Problem Ducts
Disconnected, Torn, or Damaged Ducts
Squashed
Holes/Tears
Disconnected

## Slide 8: Telltale Signs of Problem Ducts
Branch To Nowhere
Abandoned Ducts

## Slide 9: Duct Sizing
Duct Design Basics
http://www.acca.org/certification/qtech

## Slide 10: Telltale Signs of Problem Ducts
Inadequate Return Duct
Supply Duct
Return Duct

## Slide 11: Telltale Signs of Problem Ducts
Inadequate Supply Duct
Supply Duct
Return Duct

## Slide 12: Telltale Signs of Problem Ducts
Evidence of Supply and/or Return Duct Leakage
Supply Duct
Return Duct
Leakage

## Slide 13: General Air Leaks

## Slide 14
Heat to
Building
100
Furnace
Losses
43
Total Fuel
Energy
197
System
Interactions
Conduction
Leakage
54
Equipment Efficiency
100 ÷ 197 X 100 = 50.76%

## Slide 15: Building Spaces Used As Ducts

## Slide 16: Opportunities in New Buildings
ANSI/ACCA 5 QI-2015 HVAC Quality Installation Specification

## Slide 17: Lessons Learned
You should now be able to explain items to include on a duct sketch.
You should now be able to explain how bad ducting can influence HVAC system efficiency.
You should now be able to explain why some locations are better efficiency-wise for installing duct work.