## Slide 1: Technician’s First Guide and Workbook Section 14: System Installation Basics (2)

## Slide 2: Installing Thermostats
To be Americans with disabilities compliant they should be installed at 5ft. above the floor level. They should be hung level following the manufacturer’s directions. Additionally, thermostats should not be installed:
Where there are drafts.
In dead airflow spots.
In hot or cold air pathways near diffusers.
In areas where the sun hits the thermostat.
In areas not served by the equipment being controlled.
Outside walls.

## Slide 3: Thermostat Wire (2-4-6-8)

## Slide 4: Thermostat Mounting

## Slide 5: Thermostat Connections To System

## Slide 6: Swaging Refrigerant Tubing

## Slide 7: Brazing Refrigerant Tubing

## Slide 8: Brazing Refrigerant Tubing

## Slide 9: Brazing Refrigerant Tubing

## Slide 10: Leak Testing

## Slide 11: Service Valves (Condenser)

## Slide 12: Vacuum Pump

## Slide 13: Attaching Refrigerant Gauges
The valve ports will generally have Schrader valves that are designed to act like a check valve and only allow the refrigerant to flow one way unless held open.

## Slide 14: Attaching Refrigerant Gauges
Red Lines attach to the high pressure side.
Blue Lines attach to the low pressure side.

## Slide 15: Attaching Refrigerant Gauges
The best practice is to have the refrigerant lines in the gauge set filled with the same refrigerant as there is in the unit they are being connected to. To accomplish this:
Remove access covers from the access valves and ports. Note: Use two wrenches so the copper piping is not stressed or twisted.
Connect the yellow common gauge set line to a refrigerant tank (must be the system’s refrigerant).
Make sure the gauge set valves to the high (red) side and the low (blue) side are closed.
Open the refrigerant tank valve.
Crack open the high side gauge set valve a crack and vent the hose by letting a small amount of refrigerant out of the red hose (may need to push in on the check valve if one is present). Then close the gauge valve and attach hose to condenser high side access valve.
Crack open the low side valve and vent the low side hose. Close the low side gauge set valve and attach the hose to the low side condenser access valve.

## Slide 16: Removing Refrigerant Gauges
Make sure the refrigerant tank valve is closed.
Make sure the equipment is operating.
Backseat the equipment access high side valve (close off).
Crack open the gauge set high side valve, so the refrigerant can go into the yellow line.
Crack open the gauge set low side valve, so the refrigerant can go into the condenser through the suction line.
When the system pressure levels out to the low side (blue) pressure backseat the low side valve.
The gauge set can now be removed. It still will have a small amount of refrigerant left in the lines that can be left there until the next usage unless the next job uses a different refrigerant.
Put covers back on access ports and valves again using two wrenches so the pipe will not be stresses or bent.

## Slide 17: Lessons Learned
You should now be able to explain how a thermostat is wired and connected to the system.
You should now be able to explain why pulling a vacuum and testing for leaks is important.
You should now be able to explain how a refrigerant access valve works.
You should now be able to safely connect a refrigerant gauge set to a HVAC system.
You should now be able to safely disconnect a refrigerant gauge set from a HVAC system.