## Slide 1: Technician’s First Guide and Workbook Section 17: Maintenance Inspection Basics (1)

## Slide 2: Maintenance Inspection
Maintenance inspections are often done by entry level technicians who have a basic knowledge of HVAC systems and can verify the equipment is clean and operating safely. ACCA recommends Maintenance be based on the ANSI/ACCA 4 QM -2019 Maintenance of Residential HVAC Systems. Maintenance plan offerings vary among contractors. For example, some will include filter changes and coil cleaning others may charge extra for those two as an additional service. This chapter will focus on the general inspection items in the 4 QM that should be done on all HVAC system maintenance inspections. Generally, a technician will work with someone else on their first couple of maintenance inspections so they can learn the way their company wants the inspections done.

## Slide 3: Air Distribution System ESP
The first thing checked in the air distribution system for most maintenance calls is the filter. Most plans include a filter change. It is recommended that the equipment’s external static pressure (ESP) be measured and recorded after the filter is changed. If it is the same as it was recorded during the equipment startup, that means the coils are clean and the blower is performing properly.

## Slide 4: Duct & Diffuser Inspection Items
Other items for the air distribution system that are cleaned and inspected to make sure there are no repairs needed include the following:
Air filter housing and air seal integrity.
Grilles and Registers.

## Slide 5: Mold on Register

## Slide 6: Duct & Diffuser Inspection Items
Accessible duct work for cleanliness and tightness of joints and seams.
Accessible duct insulation.
Accessible duct strapping and hangers.

## Slide 7: Mold in Duct and Duct Connections

## Slide 8: Steam & Hydronic System Inspection
Fluid flow must be verified through the system. Steam and hydronic system inspections are primarily done to loo for signs of leakage or for signs of dirt or corrosion fouling up the safety valves or drain valves. Items to be inspected for cleanliness and signs of corrosion leaks, or damage include:
Safety valves.
Piping, piping insulation, and piping anchors and hangers for support defects.
Blowdown drain valve.
Steam Traps Note: not found in Hydronic Systems they hold back steam for heating while allowing water to return to the boiler.
Pumps and controls.
Heat exchangers, and radiators to include inlet outlet valves/connections and auto vents.
Strainers.

## Slide 9: Blow Down Valve

## Slide 10: Steam Trap

## Slide 11: Strainer

## Slide 12: Controls & Safeties
Inspection tasks for controls and safeties are as follows:
Test modes of operation (heat and cooling all stages)
When there are zoning controls and dampers (see Figure 103 center) test all zone controls to make sure they are operating properly.
Test thermostats and remote-control thermostats to make sure they are operating properly.
For systems with a defrost cycle test to see it functions.
Test drain pan safety switches (see figure 103 right).
Test unit safety switches. For example, furnace vent pressure switches.
Verify control settings are correct.

## Slide 13: Short In System

## Slide 14: Control Damper

## Slide 15: Safety Drain Pan Float Switch

## Slide 16: Lessons Learned
You should now be able to explain why a maintenance inspection is needed.
You should now be able to explain why an ESP test is done after changing the filter.
You should now be able to explain what a filter screen is and how to clean it.
You should now be able to explain why controls need to be inspected.
You should now be able to explain what a condensate overflow safety is and how it works.