## Slide 1: Technician’s First Guide and Workbook Section 20: Maintenance Inspection Basics (4)

## Slide 2: Fan Coil Unit (1)
Inspect the cabinets for required clearance and damage. Make sure they are correctly assembled and do not leak air:
Inspect electrical disconnect box to make sure fuse/breaker size are correct(if applicable) and connections are tight.
Ensure the cabinet is properly grounded.
Measure and record line voltage.
Inspect contactors and relays, record when there are pitted points.
Inspect electrical connections report signs of overheating such as discoloration of wire coating near connections.

## Slide 3: Fan Coil Unit (2)
Inspect capacitors, report any signs of damage. Note: many technicians test the capacitor to verify they are supplying the required microfarads.
If a capacitor goes bad there will likely be damage to the motor over time. Thus, changing out bad capacitors before they fail should increase a motor’s life expectancy.
Compare the measured operating motor amperage and voltage to the name plate rating
Verify the variable speed drive is operating properly (if applicable)
Verify proper airflow across the heating/cooling coil.
Clean coil/heat exchanger as needed and be sure coil cleaner is rated for indoor usage.

## Slide 4: Fan Coil Unit (3)
Inspect belts and pulleys for wear, and proper operation Adjust/replace as needed.
Verify fan blade is tightly connected to the shaft.
Confirm fan pulley is tightly connected to the shaft and inspect for free operation. Grease/oil as required.
Inspect coil, fittings and components clean coil and repair fins as needed.
Measure and record temperatures on both sides of the heat exchanger.

## Slide 5: Belt Adjustment

## Slide 6: Fan Coil Unit (4)
Inspect piping insulation report damage areas.
Inspect condensate drain and make sure it is installed and operating properly clean as needed.
Inspect coil and drain pan for biological growth and clean as needed.
If supplemental heat is present, verify voltage amperage and proper sequence of operation as you would for an electric furnace.

## Slide 7: Slime Growth On Evaporator Coil

## Slide 8: Boiler Maintenance Inspection
For boilers will first cover common elements for electric, gas, and oil boilers, and then cover items specific for each type in separate sections. Once again, we start by inspecting the equipment housings for required clearance and for visible damage. Make sure they are correctly assembled and leveled within the OEM’s specifications.

## Slide 9: Boiler Electrical Inspection (1)
Check the following electrical system components:
Inspect electrical disconnect box to make sure fuse/breaker size are correct(if applicable) and connections are tight.
Verify the equipment grounding is correct and tight.
Measure and record Line voltage.
Inspect and test contactors, safety/control devices.

## Slide 10: Boiler Electrical Inspection (2)
Inspect electrical disconnect box to make sure fuse/breaker size are correct(if applicable) and connections are tight.
Inspect motor capacitors for damage.
Inspect and test contactors, safety/control devices and relays.
Inspect motor capacitors for damage.

## Slide 11: Boiler Hydronic Systems (1)
Check the following hydronic system components:
Inspect and clean screens on pressure reducing valves and Y strainers.
Test bladder expansion tank for correct pressure. Check for proper air “cushion” (space) in an air pressure expansion tank.

## Slide 12: Boiler Hydronic Systems (2)
Inspect water circulating pump looking for signs of leaks or excessive vibrations.
Note: Air in the system may cause a centrifugal pump to “lose prime” (have not water going in) and to cavitate and quit circulating water. In a worst case it will destroy the pump because the water going through the pump cools down the bearings.

## Slide 13: Boiler Hydronic Systems (3)
Measure temperature differential between the boiler water entering the system and the water returning from the system and record it in the records.
Measure the pressure of the water entering the system and the water returning from the system. Then calculate the system pressure drop and record it in the records. Note: auto vents are not used on systems with air cushion tanks, an air separator removes the air from the water and allows it to go up into the sealed tank where water can expand as it is heated.

## Slide 14: Boiler Hydronic Systems (3)
Measure temperature differential between the boiler water entering the system and the water returning from the system and record it in the records.
Measure the pressure of the water entering the system and the water returning from the system. Then calculate the system pressure drop and record it in the records. Note: auto vents are not used on systems with air cushion tanks, an air separator removes the air from the water and allows it to go up into the sealed tank where water can expand as it is heated.

## Slide 15: Lessons Learned
You should now be able to explain why a capacitor that has changed shape needs to be changed.
You should now be able to identify slime on an evaporator coil.
You should now be able to identify safety controls.
You should now be able to explain what needs to be inspected in a hydronic system inspection.