## Slide 1: Technician’s First Guide and Workbook Section 23: Appendices (2)

## Slide 2: Appendix B: Filtration Primer
Filters are designed to remove particulate contaminants from the air. Some of these particulates come from natural sources such as plants, mold, fires, small insect parts, or dust from soil erosion. Manmade sources that add particulate matter to the air include car exhaust, devices that burn fossil fuel, industrial processes, etc. Generally, the smaller and lighter the particulate, the longer it will stay suspended in the air. Most airborne particles are harmless. However, some particulates - like microorganisms, droplet nuclei, and spores from fungi - can cause an allergic reaction and/or illness for some people. Breathing in industrial particulates like asbestos, coal dust, lead dust, and silica, can be a serious health risk and can cause permanent lung damage.

## Slide 3: Basic Filtration
Most HVAC systems are designed to utilize basic filtration (primarily intended to protect coils and heat exchangers from relatively large dust particulates). As the air passes through the filter material, large particulates become trapped. If, due to environmental or health concerns, protection from smaller particulates is required, the filter will need to be more efficient (able to remove smaller particles). In order to maintain the required airflow, HVAC equipment design modifications often are required when a filter change is made due to the change in filter resistance (called “pressure drop”).

## Slide 4: Panel Filters
Panel Filters: Where the face air velocity and media air velocity are identical:
Fiberglass or synthetic media in a disposable cardboard frame with metal or synthetic backing material.
Synthetic ring or link panels
Aluminum or synthetic washable media panel frame filters

## Slide 5: Extended Surface Filters
Extended Surface Filters: Where face air velocity is always higher than the media air velocity:
Pleated filters
Pocket Filters (also known as bag filters) utilizing either lofted micro-fiberglass or synthetic media
Rigid Box or Rigid Cell filters utilizing either lofted micro-fiberglass, synthetic or wet-laid micro-fiberglass media.

## Slide 6: Electronic Air Cleaners
Electronic Air Cleaners: Also known as Electrostatic Precipitators.
They remove gas and fine particles from an airstream by use of an electrostatic charge that slows down airflow.

## Slide 7: HEPA Air Filters
High Efficiency Particulate Air (HEPA): Filters that have a minimum efficiency of 99.97% when challenged with appropriate substance and specific flow rate. This category also includes Ultra Low Penetration Air (ULPA) Filters – 99.999% and Super Ultra Low Penetration Air (SULPA) Filters – 99.9999%+.

## Slide 8: Typical Filter Material
Filters are generally fabricated by combining fibers into non-woven media sheets. Common filter materials include:
Large fiber synthetic media such as polyester or polypropylene (can be passive electrostatic and / or cleanable)
Fiberglass which includes large strand or micro-glass media
Small fiber electrostatically charged synthetic media.

## Slide 9: Special Application Filter Material
Synthetics impregnated with carbon (for odor control)
“Hog Hair” made from washable interconnected natural fibers coated with vinyl and used in wet environments or where filter materials have to conform to differing shapes.
Metal filters made with aluminum, stainless steel, steel black wire, mesh-perforated-screen media used for gross filtration of outdoor air (bug screen) or high heat applications.

## Slide 10: Filter Pressure Drop

## Slide 11: Typical OEM Filter Pressure Drop Chart
Filter Air Resistance Furnace XYZ (for 1-inch cleanable filter field provided) |  |  |  |  | 
CFM | 200 | 400 | 800 | 1000 | 1200
In. w.g. | 0.01 | 0.03 | 0.06 | 0.09 | 0.12

## Slide 12: Particulate Removal Efficiency

## Slide 13: Filter Application Guide
Std 52.2 MERV | Average ASHRAE Dust Spot Efficiency Std 52.1 | Average ASHRAE Arrestance Std 52.1 | Particle Size Ranges | Typical Applications | Typical Filter Type
1-4 | <20% | 60 to 80% | > 10.0 µm | Residential / Minimum Light / Commercial Minimum / Equipment Protection | Permanent / Self Charging (passive) Washable / Metal, Foam / Synthetics Disposable Panels Fiberglass / Synthetics
5-8 | <20 to 35% | >80 to 95% | 3.0 - 10.0 µm | Industrial Workplaces Commercial Better / Residential/ Paint Booth / Finishing | Pleated Filters Extended Surface Filters Media Panel Filters
9-12 | 40 to 75% | >95 to 98% | 1.0 - 3.0 µm | Superior / Residential Better / Industrial Workplaces Better / Commercial Buildings | Non-Supported / Bag Rigid Box Rigid Cell / Cartridge
13-16 | 80 to 95% + | >98 to 99% | 0.30 - 1.0 µm | Smoke Removal General Surgery Hospitals & Health Care Superior / Commercial Buildings | Rigid Cell / Cartridge Rigid Box Non-Supported / Bag
17-201 | 99.972 99.992 99.9992 | N/A | ≤ 0.30 µm | Clean Rooms High Risk Surgery Hazardous Materials | HEPA ULPA

## Slide 14: Existing Filter Installation Problems
A filter that is too large will rarely cause an operational problem for an HVAC system. However, an undersized filter can cause airflow problems. For existing equipment where a specific width filter rack is installed, corrective options for increasing the filter’s area are decreased. One possible solution is to convert to a pleated filter. Due to their design, the surface areas for pleated filters can be 4 to 5 times larger than surface areas of a conventional filter that has equivalent outside dimensions. For example: based on the 28 x 24 filter slot from the example above, a pleated filter with a surface area four times greater than the original standard flat filter with the same outside dimensions, and fits into the same 1” width rack, could have a surface area four time larger or: 4 x 28 x 24 = 2688 in2 or 18.66 ft2.

## Slide 15: Warning!
Avoid a trap: The solution I just provided looks good at first, but caution must be taken. Many pleated filters advertise increased efficiency. However, filters designers equate greater efficiency with the filtration of more and smaller particulate. Therefore, the increase in surface area does not automatically equate to a smaller pressure drop across the filter. A pressure drop chart for the pleated filter should be consulted to evaluate how the increased area relates to actual CFM at the specified pressure drop in IWC.

## Slide 16: Ultraviolet Germicidal Irradiation (UVGI)
UVGI lights are not filtration devices but are often used in conjunction with filters. UVGI sizing is based on the amount of airflow moved within the HVAC system in CFM. UVGI lights generally will not affect the total airflow in an HVAC system. UV lights are often installed in systems that have a history of slime, mold, or mildew on the coils. Because biological organisms can be smaller than 0.1 micrometers, installing filters to remove them from HVAC systems may not be a viable alternative due to increased pressure drop.
UVGI works by penetrating biological cells and breaking down the molecular bonds in them. Breaking down the molecular bonds causes mutations that result in genetic damage that makes the microorganisms unable to reproduce and non-viable.

## Slide 17: Ultraviolet Germicidal Irradiation (UVGI)
It is important when selecting UVGI lighting systems to know the bulbs life expectancy. Over time the bulbs lose their ability to provide the required level of light (wavelength of 2,537 Angstroms or 254 nanometers). To work properly, it is important to maintain a UVGI wattage level high enough to remain effective. Since the bulbs loose effectiveness when operating over time, it is important to change the bulbs at the required intervals.
The location of the bulbs is also an important design consideration. Since UVGI may deteriorate coatings on electric wiring, duct liner, and media in air filters where the light is applied is an important design consideration. All technicians must be instructed to make sure the UVGI lights are off when they are servicing the equipment because they can quickly damage skin and eyes.

## Slide 18: Lessons Learned
You should now be able to explain the difference between filter efficiency and how it may change the HVAC system’s efficiency.
You should now be able to identify filter related problems with an HVAC system.
You should now be able to name sever types of filter options for those who want better filtration.
You should now be able to use the tables to identify what MERV is required for a type of particulate that needs to be filtered out.