## Slide 1: Technician’s First Guide and Workbook Section 8: Electrical Components and Electrical Measurement Part 2

## Slide 2: Door and Cabinet Switches

## Slide 3: Ohm Testing Switches Power Off

## Slide 4: Relay/Switch Testing Voltage & Amperage

## Slide 5: Evaporator Blower Motors

## Slide 6: Evaporator Blower Motors Speed Setting

## Slide 7: Capacitors

## Slide 8: Two In One Capacitor

## Slide 9: Capacitor Testing

## Slide 10: Compressor

## Slide 11: Condenser Fan Motor

## Slide 12: Electrical Resistance Heat

## Slide 13: Watts
The formula for evaluating kilowatt output is based on the accurate field measurements of amps and volts:
W = V × I
Where:
W= watts (power) Note kW = 1000 watts
V= Voltage
I = amperage

## Slide 14: Calculating Watts With Field Measured Amperage and Voltage (1)
Example a furnace is rated at 5kW and has a measured 240V input voltage. What amperage would verify the heater is operating properly?
5,000 = 240 × I OR: I = 5,000 ÷ 240 = 20.83 amps

## Slide 15: Calculating Watts With Field Measured Amperage and Voltage (1)
If a technician measured 238V at 22 amps in the field is the 5kW heater working properly?
W = 238 × 22 = 5,236 Watts or 5.236 KW
5.236 ÷ 5 × 100 = % of design watts = 104.72% (since that is within 5% the system is operating correctly).

## Slide 16: Control Board

## Slide 17: Grounding/Bonding

## Slide 18: Wire Nuts

## Slide 19: Slip In & Spade Wire Connectors

## Slide 20: Wire Strippers and Crimpers

## Slide 21: Wire Blocks

## Slide 22: Lessons Learned
You should now be able to measure amperage using a meter.
You should now be able to measure voltage using a meter.
You should now be able to identify methods for connecting wires and be capable of using them to connect wires.
You should now be able to use an ohm-meter to verify if a switch is good or bad.
You should now be able to explain how to test a capacitor for µF.
You should now be able to calculate watts given voltage and amperage.