## 2009 BCGs
Unit Rates for Gross Replacement Costs (GRC)
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Electrical Services | Distribution Boards | Distribution Boards |  |  | no | 40 | 30 | 50 | 1 | 5 | 4
|  | Local DBS | 9 pole single phase | 48 way 144 pole three phase with controls | no | 40 | 32 | 48 | 1 | 5 | 4
|  | Main Fusebox | 9 pole single phase | 12 way 36 pole three phase | no | 40 | 32 | 48 | 1 | 5 | 4
|  | Main Switch Board | Small | Large public building | no | 40 | 32 | 48 | 1 | 5 | 4
|  | Mechanical Services Switch Board |  |  | no | 40 | 32 | 48 | 1 | 5 | 4
|  | Meter Boxes | Hicks HP1 | Hicks HP7 | no | 40 | 32 | 48 | 1 | 5 | 4
| Emergency Lighting (Not fire related) | Batteries | Light | Heavy | sum | 18 | 15 | 20 | 1 | 5 | 5
|  | Controller / Cabling | Light | Heavy | sum | 25 | 20 | 30 | 2 | 5 | 5
|  | Lamps |  |  | sum | 13 | 10 | 15 | 3 | 5 | 5
| Emergency Power | Fuel Tank |  |  | no | 43 | 35 | 50 | 1 | 5 | 4
|  | Gen Set - alternator |  |  | no | 35 | 30 | 40 | 1 | 5 | 4
|  | Gen Set - engine |  |  | no | 43 | 35 | 50 | 1 | 5 | 4
| Lighting - External/Internal | Controller / Cabling | Light | Heavy | sum | 40 | 30 | 50 | 1 | 3 | 2
|  | Down Lights |  |  | no | 15 | 12 | 18 | 4 | 3 | 3
|  | Exit Signs | Thorn ECON110S | Stanilite LSNCS122 Legend Maint Monitored | no | 18 | 15 | 20 | 5 | 5 | 4
|  | Fittings |  |  | sum | 18 | 15 | 20 | 3 | 3 | 3
|  | Fluorescent Lights | Fluorescent, batten, 2x36w | Fluorescent, recessed, grid ceiling, 3x36w | no | 25 | 20 | 30 | 4 | 4 | 3
|  | Incandescent Lights | Batten lampholder | Pendant, 3 light type | m2 | 18 | 15 | 20 | 4 | 5 | 3
|  | Lamps |  |  | sum | 14 | 12 | 15 | 4 | 3 | 3
| Lighting - Flood / Security | Controller / Cabling | Light | Heavy | sum | 40 | 30 | 50 | 1 | 4 | 4
|  | Fittings |  |  | sum | 18 | 15 | 20 | 3 | 4 | 4
|  | Lamps |  |  | sum | 14 | 12 | 15 | 3 | 4 | 3
|  | Local Security Lighting | Batten lampholder | 2000 watt metal halide discharge | no | 18 | 15 | 20 | 4 | 5 | 4
|  | Pole Top Lights (External) | 80 watt mercury in 550 dia opal sphere | Bega 150 watt sodium on 7.6 m. pole | no | 18 | 15 | 20 | 4 | 5 | 4
| Misc. | Light Switches & Powerpoints | Light | Heavy | m2 | 30 | 24 | 36 | 2 | 4 | 4
| Power Conditioning | Batteries |  |  | sum | 18 | 15 | 20 | 1 | 4 | 4
|  | Chargers |  |  | sum | 25 | 20 | 30 | 1 | 4 | 4
|  | UPS |  |  | no | 35 | 30 | 40 | 1 | 4 | 4
| Power Conversion | Power conversion |  |  | sum | 38 | 35 | 40 | 1 | 4 | 3
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Exterior Works | Buildings | Carport | Conc slab,timber frm, galv steel roof (kitset) | Higher quality including Colour steel | m2 | 50 | 40 | 60 | 2 | 2 | 2
|  | Covered Ways | .4mm Endura corrugated | .9mm aluminium trough 300 profile | m2 | 55 | 45 | 70 | 3 | 3 | 4
|  | Garage | 6x3.5m Conc, timber frame, galv steel clad | Ditto, brick veneer, conc tile roof | m2 | 50 | 40 | 60 | 4 | 4 | 3
|  | Shed (Garden / Tool Shed) | kitset on conc slab | Ditto, brick veneer, conc tile roof | no | 20 | 15 | 25 | 2 | 4 | 2
|  | Sun Screen/Awning | Roll up awnings, canvas | Fixed awnings, canvas | ea | 15 | 10 | 20 | 3 | 3 | 4
|  | Verandah - Roof Only | .4mm Endura corrugated | .9mm aluminium trough 400 profile | m2 | 55 | 45 | 70 | 3 | 3 | 4
| Channels | Channels & Grating | P'cast channel 225wide& 50 th.grate | P'cast channel 450wide& 75 th.grate | m | 45 | 35 | 50 | 2 | 3 | 2
|  | Kerb & Channelling | 75 wide kerb, 300 wide channel | kerb and channel, 250 x 300 wide | m | 40 | 35 | 50 | 2 | 2 | 2
| Civil works | Block Wall | 150 block, footing no finish | 250 block, footing, no finish | m2 | 75 | 60 | 90 | 2 | 4 | 3
|  | Brick Wall | 100 thick | 200 thick | m2 | 50 | 40 | 60 | 2 | 4 | 3
|  | Retaining Walls (Concrete) | 600 max ret, Grip block precast interlocking | 7400 max ret, Grip block precast interlocking | m2 | 75 | 60 | 90 | 2 | 4 | 4
|  | Retaining Walls (Timber) | 1800 max retaining, Timbercrib | 6300 max retaining, Timbercrib | m2 | 60 | 45 | 72 | 2 | 4 | 4
| Fencing | Corrugated Iron Fence | .4 thick corrugated steel | .4 thick corrugated steel and timber frame | m2 | 25 | 20 | 35 | 2 | 3 | 2
|  | Fence - Paint Finish | prep and one coat acrylic one side | prep and 3 coat enamel one side | m2 | 10 | 8 | 12 | 3 | 4 | 1
|  | Picket Fence | 1400 high timber | metal 1400 high, galv welded fence panels | m | 25 | 20 | 35 | 4 | 3 | 2
|  | Post & Rail Fence | 1500 high, 150 x 19 timber paling | 1800 high, 150x 25 timber palings | m | 25 | 20 | 35 | 2 | 3 | 2
|  | Post & Wire Fence | 7 wire and posts | 8 wire posts, battens | m | 25 | 20 | 35 | 2 | 3 | 2
|  | Post / Rail / Mesh Fence | 1800 high galv mesh | 2700 high, pvc coating, top rail, mowing strip | m | 25 | 20 | 35 | 2 | 3 | 2
|  | Steel Security fence |  |  | m2 | 25 | 20 | 35 | 2 | 5 | 4
|  | Timber Paling Fence | 1500 high 150 x 19 pailings | 1800 high 150 x 25 palings | m | 25 | 20 | 35 | 3 | 3 | 2
|  | Wire Mesh Fence | Replace wire mesh only | Replace wire mesh only | m2 | 25 | 20 | 35 | 2 | 3 | 2
| Furniture | Park Seat | 1.3m tubular frame with perforated steel top | 4 seat tubular frame with perforated steel top | no | 15 | 12 | 18 | 3 | 3 | 3
|  | Picnic Table | 2.1m tubular frame with perforated steel top | Timber seat and table | no | 15 | 12 | 18 | 3 | 3 | 3
|  | Rubbish Bin | Semi circular wall mounted | 52 litre stainless steel | no | 15 | 12 | 18 | 3 | 3 | 4
| Gates | Metal Gate | Metal Gate | 0 | no | 50 | 40 | 60 | 3 | 4 | 3
|  | Motorised Sliding Gate | Single metal gate with motor and key pad | Double metal gate with motoe and key pad | no | 25 | 20 | 30 | 4 | 4 | 3
|  | Steel/Mesh Gate | 1000 x 1800 high single | 4800 x 1800 high double | no | 25 | 20 | 35 | 3 | 4 | 3
|  | Timber Gate | Rough sawn single gate 1500 x 1800 high | Double T & G ornate timber gate | no | 25 | 20 | 30 | 3 | 4 | 3
|  | Wrought Iron Gate | Standard single gate | Ornate double gate | no | 50 | 40 | 60 | 4 | 4 | 3
| Hard stand | Asphalt /Sealed Areas | 2 cts bitumen and metal chip surfacing | 250 basecourse,40thick asphalt | m2 | 12 | 10 | 15 | 4 | 3 | 3
|  | Asphalt Paths | 20 thick asphalt | 40 thick asphalt | m2 | 12 | 10 | 16 | 3 | 4 | 3
|  | Astro Turf | synthetic turf | sportsflex sports flooring | m2 | 10 | 8 | 12 | 4 | 4 | 2
|  | Carpark Marking | Typical application | Typical application | m | 5 | 4 | 6 | 2 | 4 | 2
|  | Cobblestone | 45 thick | 60 thick (23m2) with 100 thick basecourse | m2 | 25 | 20 | 30 | 4 | 3 | 3
|  | Concrete Paths / Ramps | 150 thick path | 200 thick path 100 thick subbase | m2 | 55 | 45 | 65 | 3 | 4 | 4
|  | Concrete Paver / Interlocking Blocks | 300 x 300 x 40 paving | 80mm conc brick pav,on 250 basecourse | m2 | 50 | 40 | 60 | 3 | 3 | 3
|  | Concrete Slab | 75 thick conc unreinforced | 125 conc on 250 hardfill, reinf, edge thickening | m2 | 50 | 40 | 60 | 3 | 3 | 3
|  | Timber Kerbs | Base parking barrier | Heavy duty barrier | m | 25 | 20 | 30 | 3 | 3 | 4
| Misc. | Decking | Pine decking | Hardwood decking | no | 25 | 15 | 40 | 3 | 3 | 3
|  | Paint | Paint to ext walls, incl prep. 2 coat acrylic | waterblast surface, textured finish | m2 | 10 | 8 | 14 | 4 | 4 | 1
|  | Shade Cloth | Woven nylon in green excluding frame | Woven nylon in white excluding frame | m2 | 15 | 14 | 16 | 4 | 3 | 4
| Signs | Sign (Exterior) | Sign, exterior, building signage, basic | Sign, exterior, building signage, high quality | no | 10 | 8 | 12 | 5 | 4 | 2
|  | Sign (Route) | Sign, exterior, route/direction, basic | Sign, exterior, route/direction, high quality | no | 10 | 8 | 12 | 5 | 4 | 2
|  | Sign (Timber) | Sign, interior, route/direction, basic | Sign, interior, route/direction, high quality | no | 10 | 8 | 12 | 5 | 4 | 2
| Stairs & rails | Handrail Metal | 45 dia aluminium wall mounted | 50 dia brass wall mounted | m | 50 | 40 | 60 | 4 | 4 | 1
|  | Handrail Timber | 100 x 50 pine wall mounted | 45 dia Rimu wall mounted | m | 50 | 40 | 60 | 4 | 4 | 1
|  | Staircase - Metal | 1000 wide straight | 1500 dia spiral stair | m/H | 60 | 50 | 70 | 3 | 4 | 4
|  | Staircase - Timber | 900 wide pine | 1000 wide pine with balustrade one side | m/H | 50 | 40 | 60 | 3 | 4 | 4
| Water tanks | Water Tank - Concrete | 4500 litre concrete water tank | 22700 litre concrete water tank | no | 60 | 45 | 75 | 2 | 5 | 4
|  | Water Tank - Metal | 9,000 litre galv steel water tank | 18,800 galv steel water tank | no | 60 | 45 | 75 | 2 | 5 | 4
|  | Water Tank - Plastic | 135 litre | 5000 litre | no | 50 | 35 | 65 | 2 | 5 | 4
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
External Fabric | External Walls | Brick Cladding | 70mm veneer Firth classic. No finish | 70mm veneer Monier cotswold. No finish | m2 | 75 | 60 | 90 | 4 | 3 | 1
|  | Curtain Walling (Glass) | Alum. 50% clear glass 50% armourclad | more difficult installation | m2 | 55 | 45 | 75 | 4 | 3 | 2
|  | Fibrolite Sheeting | Hardiflex | Titan 9mm wall board, primed, epoxied, jointed, battens behind | m2 | 50 | 40 | 65 | 4 | 3 | 2
|  | Hardiplank | 240 smooth | 240 vertical and 180 under | m2 | 50 | 40 | 60 | 4 | 3 | 2
|  | Marble | 300 x 300 x 10 tiles | 20 thick panels | m2 | 100 | 80 | 120 | 5 | 3 | 1
|  | Metal Cladding | .75 thick galv sheet | 1 mm thick electro galvanised | m2 | 35 | 20 | 45 | 4 | 3 | 1
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 12 | 4 | 4 | 1
|  | Plaster | 2 ct wood float | Tyrolean | m2 | 50 | 40 | 60 | 3 | 4 | 1
|  | Plywood | 7 thick plywood | 21 thick plywood | m2 | 50 | 45 | 75 | 3 | 3 | 2
|  | Precast Concrete Wall Panels | 125 thick | 200 thick | m2 | 100 | 80 | 150 | 4 | 3 | 2
|  | Pvc Weatherboards | Certainteed rusticated | Palliside rusticated | m2 | 35 | 30 | 40 | 4 | 3 | 2
|  | Shiplap | 200 x 25 cedar | 150 x 25 cedar | m2 | 75 | 60 | 90 | 4 | 3 | 2
|  | Weatherboard - Timber | 150 x 25 pine | 200 x 25 cedar | m2 | 75 | 60 | 90 | 4 | 3 | 2
| Roof | Butynol Roofing | 1 thick black incl replace plywood | 1.5 thick grey including replace plywood | m2 | 20 | 16 | 24 | 4 | 4 | 2
|  | Colorbond |  |  | m2 | 30 | 15 | 45 | 3 | 3 | 2
|  | Compressed Fibre | 9mm thick Hardipanel | 18mm thick Hardipanel | m2 | 50 | 40 | 65 | 3 | 3 | 2
|  | Concrete Roof Slabs | 75 thick | 150 thick | m2 | 100 | 75 | 150 | 3 | 3 | 2
|  | Downpipes - Metal | 65 dia zincalume steel | 100 dia S.S. | m | 35 | 25 | 45 | 2 | 3 | 1
|  | Downpipes - Pvc | 65 dia PVC | 100 dia PVC | m | 35 | 25 | 40 | 2 | 3 | 1
|  | Glass | Clear polycarbonate | Tinted polycarbonate | m2 | 50 | 40 | 60 | 4 | 4 | 2
|  | Metal Roofing | 0.4mm zincalume corrugated | .9mm aluminium trough 400 profile | m2 | 30 | 15 | 45 | 4 | 4 | 2
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 14 | 4 | 3 | 1
|  | Safety access system - anchor points |  |  | no | 20 | 18 | 25 | 2 | 5 | 5
|  | Safety access system - walkways |  |  | sum | 20 | 18 | 25 | 2 | 5 | 5
|  | Shingles - Timber | Treated pine shingles | Cedar shingles more difficult installation | m2 | 35 | 30 | 42 | 3 | 3 | 2
|  | Skylight | 610sq Adlux low profile spandrome nonvent. | 2075 x 2075 Adlux pyramid spandome | m2 | 50 | 40 | 60 | 3 | 4 | 2
|  | Soffits - Fibrolite | Hardiflex, 4.5mmPVC mouldings | Silkline Prefinished Soffit Linings & Working at height | m2 | 50 | 40 | 60 | 3 | 1 | 1
|  | Soffits - Timber | 7 thick plywood | 12 thick pine | m2 | 55 | 45 | 75 | 3 | 1 | 1
|  | Spouting - Metal | 125 zincalume steel | 125 copper | m | 35 | 25 | 45 | 2 | 4 | 1
|  | Spouting - Pvc | 125 dia PVC | Magnum 170mm half round gutter | m | 35 | 25 | 40 | 2 | 4 | 1
|  | Tile Roofing - Clay | Portoghese clay tile | French profile clay tile | m2 | 60 | 50 | 80 | 4 | 3 | 2
|  | Tile Roofing - Concrete | Rosscrete hacienda to single storey | Monier to 3 storey | m2 | 90 | 75 | 120 | 4 | 3 | 2
|  | Tile Roofing - Slate | Resin bonded reconstituted slate | Welsh slate | m2 | 100 | 80 | 120 | 4 | 4 | 2
|  | Timber Fascia | 150 x 25 | 250 x 40 thick | m | 50 | 40 | 60 | 3 | 3 | 2
|  | Translucent Sheeting | PVC sheeting | Duralite fibreglass | m2 | 25 | 20 | 30 | 4 | 3 | 2
| Windows & Doors | Alum Frame Glass - Dble Door | 1980x1620 dble with 6 thick toughened glass | Larger doors, higher specification | no | 55 | 45 | 65 | 4 | 4 | 2
|  | Alum Frame Glass - Sgle Door | 1980x810 single with 6 thick toughened glass | Larger doors, higher specification | no | 55 | 45 | 65 | 4 | 4 | 2
|  | Alum/Glass - Sliding Dble Door | 1980x1620 dble with 6 thick toughened glass | Larger doors, higher specification | no | 55 | 45 | 65 | 4 | 4 | 2
|  | Alum/Glass - Sliding Sgle Door | 1980x810 sgle with 6 thick toughened glass | Larger doors, higher specification | no | 55 | 45 | 65 | 4 | 4 | 2
|  | Aluminium Windows | Single glazed | Double glazed | m2 | 55 | 45 | 65 | 3 | 4 | 3
|  | Automatic Opening Doors | Single glazed - elect. lock/beam/mat switch | 3leaf/bifolding - elect. lock/beam/mat switch | no | 25 | 20 | 30 | 5 | 5 | 4
|  | Door Hardware (Handles/Locks) | basic lever style | High quality | no | 30 | 25 | 40 | 3 | 4 | 4
|  | Emergency Exit Door - Double | Standard style doors | Larger doors | no | 65 | 50 | 85 | 5 | 5 | 1
|  | Emergency Exit Door - Single | Standard style door | Larger doors | no | 65 | 50 | 85 | 5 | 5 | 1
|  | Glass Door | Sgle 10mm tough. frameless glass doors | Larger doors | no | 55 | 45 | 65 | 4 | 4 | 4
|  | Louvre Windows | 900 x 1000 timber frame fixed | 900 x 1000 timber frame adjustable | m2 | 35 | 30 | 45 | 2 | 3 | 4
|  | Metal Clad Doors | Zintec metal clad single door | Stainless steel clad single door | no | 35 | 28 | 42 | 2 | 3 | 2
|  | Metal Framed Windows | Steel commercial over 0.5 m2 | Steel residential under 0.5 m2 | m2 | 55 | 45 | 65 | 4 | 4 | 3
|  | Metal Roller Doors | Continuous curtain | Interlocking slat | m2 | 35 | 28 | 42 | 2 | 3 | 2
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 12 | 4 | 4 | 1
|  | Roller Doors | Continuous curtain | Interlocking slat | no | 35 | 28 | 42 | 2 | 3 | 3
|  | Sliding Doors | Aluminium glazed single door | Larger door | no | 55 | 45 | 65 | 3 | 4 | 3
|  | Timber / Glass Door | Half glass and half timber | 860mm x 40mm top and sidelight panels glazed | no | 55 | 45 | 65 | 4 | 4 | 2
|  | Timber Entrance Door | Pine no finish incl frame | Fiji Kauri no finish incl frame | no | 55 | 45 | 65 | 4 | 5 | 1
|  | Timber Framed Windows | Pine | Cedar colonial | m2 | 55 | 45 | 65 | 4 | 4 | 3
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Fire Services | Fire Alarm System | Cabling |  |  | sum | 43 | 35 | 50 | 1 | 3 | 4
|  | Fire / mimic panels |  |  | no | 13 | 10 | 15 | 3 | 4 | 4
|  | Heat detectors | Typical product | Typical product | sum | 20 | 17 | 22 | 3 | 5 | 5
|  | Magnetic door holders |  |  | sum | 20 | 17 | 22 | 2 | 5 | 5
|  | Smoke detectors | Combustion type | Photo optic type | sum | 15 | 10 | 20 | 3 | 5 | 5
| Fire Communications | EWIS panel | System complete, for minor installation | System complete, major installation | no | 13 | 10 | 15 | 3 | 3 | 4
| Fire Services | Fire Extinguishers | 2.25 kg dry powder | 5 kg CO2 | no | 20 | 16 | 24 | 4 | 5 | 5
|  | Fire Hose Reels | Standard 20m x 13 dia | Surface cabinet 20m x 19 dia | no | 18 | 15 | 20 | 4 | 5 | 5
|  | Ventilating Fans | 3.5m3/s roof extract | 23 m3/s roof extract | no | 25 | 20 | 30 | 3 | 4 | 4
| Fire Sprinkler System | Pipes and valves | Fire_Pipework_25 dia, screw fittings | Fire_Pipework_150 dia, grooved end joints & fittings | sum | 50 | 40 | 60 | 1 | 4 | 2
|  | Sprinkler heads | Standard head exposed | Standard head flush mounted | sum | 30 | 24 | 36 | 3 | 4 | 4
| Hydrant System | Hydrant System |  |  | sum | 43 | 35 | 50 | 3 | 3 | 5
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Interior Finishes | Ceiling Finishes | Fibrolite | 9.5mm - fibrous plaster | 19mm - fibrous plaster | m2 | 75 | 60 | 90 | 2 | 4 | 1
|  | Gyprock Lining |  |  | m2 | 50 | 40 | 60 | 2 | 3 | 1
|  | Hardboard | 3mm hardboard | 6mm hardboard | m2 | 75 | 60 | 90 | 2 | 3 | 1
|  | Insulation | Pink batts R1.8 | Thermofleece C2 | m2 | 75 | 60 | 90 | 1 | 4 | 4
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 12 | 3 | 2 | 1
|  | Particle Board | Kopine Ultralock | Pynefloor Gold | m2 | 75 | 60 | 90 | 2 | 3 | 1
|  | Plaster Finish | Hardwall | Tyrolean | m2 | 50 | 40 | 60 | 4 | 4 | 1
|  | Prefinished Metal |  |  | m2 | 40 | 35 | 50 | 4 | 3 | 3
|  | Softboard / Pinex Tiles / Lining | 13 thick wood fibre panels | 38 thick wood fibre panels, acoustic | m2 | 50 | 40 | 60 | 2 | 3 | 1
|  | Suspended Panel (incl Frame) | Exposed suspension system with fibrous plaster acoustic tiles | Concealed suspension system with tiles | m2 | 40 | 30 | 50 | 4 | 3 | 1
|  | Suspended Panel (incl Frame), Acoustic |  |  | m2 | 50 | 40 | 60 | 3 | 3 | 3
|  | Suspended Panel (incl Frame), Plasterboard |  |  | m2 | 50 | 40 | 60 | 3 | 3 | 3
|  | Timber Lining | T & G pine | Shiplap panelling | m2 | 75 | 60 | 90 | 2 | 3 | 1
| Fixtures & Fittings | Dishwasher |  |  | no | 10 | 8 | 13 | 2 | 3 | 3
|  | Fixed Desks, Tables, Seating | Workstation, medium quality | Workstation, high quality | no | 20 | 16 | 25 | 3 | 4 | 3
|  | Fixed Seating | Base timber seating | High specification seating | no | 20 | 16 | 25 | 3 | 4 | 3
|  | Grabrails | 600mm long, 25mm dia, stainless steel | 750mm x 750mm, 32mm dia, stainless steel | no | 25 | 20 | 40 | 3 | 3 | 3
|  | Hand dryer |  |  | no | 10 | 9 | 12 | 4 | 2 | 3
|  | Handrail Stainless | 600mm long, 25mm dia, stainless steel | 750mm x 750mm, 32mm dia, stainless steel | ea | 25 | 20 | 40 | 5 | 3 | 3
|  | Holland Blinds |  |  | m2 | 40 | 30 | 50 | 4 | 3 | 3
|  | Joinery Fttgs - Built-In | Painted MDF | Melamine carcass with solid Rimu fronts | m | 40 | 32 | 48 | 3 | 3 | 3
|  | Kitchen Bench and Joinery |  |  | m | 25 | 20 | 30 | 3 | 5 | 3
|  | Kitchen Bench S/S | Unpainted MDF with SS top | Melamine with solid Rimu fronts SS top | m | 40 | 30 | 45 | 3 | 5 | 4
|  | Mirror | Clear float, 1m x 1m | 6 thick polycarbonate | ea | 20 | 16 | 30 | 4 | 3 | 3
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 12 | 4 | 4 | 1
|  | Shelving | Pine no finish | 18 thick melamine | m | 35 | 28 | 42 | 2 | 3 | 3
|  | Stoves | Average electric wall oven | De-lux gas wall oven | no | 15 | 12 | 20 | 4 | 5 | 3
|  | Towel rail |  |  | no | 15 | 10 | 20 | 1 | 1 | 3
|  | Work Benches | Laminated top | Stainless Steel top | m | 40 | 32 | 48 | 3 | 3 | 3
|  | Zip Heater | remove, 45 litre, elec connex | remove, 315 litre, elec connex | no | 25 | 20 | 30 | 4 | 4 | 3
| Floor Finishes | Carpet | Nylon loop pile, direct stick | Heavy duty Axminster, double stick underlay | m2 | 15 | 10 | 22 | 4 | 4 | 4
|  | Ceramic Tiles | Glazed quarry tiles, 300 x 300 | Ceramic mosaic tiles, 50mm x 50mm | m2 | 50 | 40 | 60 | 4 | 3 | 4
|  | Cork | Cork tiles, sanding, 3 coat polyurethane finish | Cork tiles, sanding, 4 coat poly | m2 | 25 | 20 | 30 | 4 | 3 | 2
|  | Epoxy |  |  | m2 | 15 | 12 | 20 | 4 | 3 | 3
|  | Floating Timber | 7 mm veneer system | Solid timber (20 mm) | m2 | 15 | 10 | 30 | 3 | 4 | 2
|  | Floor - Particle Board | Kopine Ultralock | Premafloor purple tongue | m2 | 75 | 60 | 90 | 2 | 3 | 2
|  | Floor - Timber T & G | Jarrah incl finish | Heart Rimu incl finish | m2 | 75 | 60 | 90 | 3 | 3 | 3
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 12 | 5 | 3 | 1
|  | Parquet | Boral Australian | NZ hardwoods | m2 | 50 | 40 | 60 | 4 | 3 | 3
|  | Polyurethane Finish | Three coats | Four coats | m2 | 10 | 8 | 12 | 4 | 3 | 3
|  | Rubber | 2 thick smooth for light traffic | 4 thick studded for heavy traffic | m2 | 35 | 28 | 42 | 4 | 3 | 3
|  | Stair Nosing | Standard for vinyl | Aluminium for carpet etc | m | 15 | 12 | 18 | 5 | 5 | 5
|  | Vinyl | 2 thick standard sheet | 5.5 thick non slip sports | m2 | 15 | 10 | 20 | 3 | 3 | 3
| Interior Doors | Accordion / Folding | Accordian doors | Larger doors | m2 | 20 | 16 | 24 | 3 | 3 | 3
|  | Alum/ Safety glass |  |  | m2 | 20 | 15 | 24 | 3 | 2 | 5
|  | Alum/ Toughened glass |  |  | m2 | 25 | 18 | 30 | 3 | 4 | 3
|  | Doors - Hollow-Core | Hollow core sgle doors incl frm plywood facing | Hollow core dble doors incl frm plywood facing | no | 35 | 25 | 40 | 3 | 3 | 2
|  | Doors - Solid | Solid core single door incl frame | Solid core double door incl frame | no | 50 | 40 | 60 | 3 | 3 | 4
|  | Fire Doors | 1/2 hour single | 2 hour double | no | 50 | 40 | 60 | 2 | 5 | 5
|  | Glass | Clear polycarbonate | Tinted polycarbonate | m2 | 50 | 40 | 60 | 3 | 4 | 3
|  | Metal Doors | Zintec metal clad single door | Stainless steel clad single door | no | 50 | 40 | 60 | 3 | 3 | 2
|  | Metal Roller Door | Continuous curtain | Interlocking slat | m2 | 35 | 28 | 42 | 3 | 3 | 2
|  | Paint Finish (Per Leaf) | Base quality typical door | High quality larger door (860x1980) | no | 10 | 8 | 12 | 5 | 3 | 1
|  | Polyurethane Finish (Per Leaf) | Base quality typical door | High quality larger door (860x1980) | no | 10 | 8 | 12 | 5 | 3 | 1
|  | Safety glass |  |  | m2 | 50 | 40 | 60 | 4 | 5 | 5
|  | Sliding Doors | Aluminium glazed single door | Larger door | no | 50 | 40 | 60 | 3 | 4 | 2
|  | Solid Core | Solid core single door incl frame | Solid core double door incl frame | no | 50 | 40 | 60 | 4 | 3 | 3
|  | Solid Core/ Glass | Solid core single door incl frame | Solid core double door incl frame | no | 50 | 40 | 60 | 4 | 3 | 3
|  | Solid Core/ Safety glass | Solid core single door incl frame | Solid core double door incl frame | no | 50 | 40 | 60 | 4 | 5 | 5
|  | Swing Doors - (Pair) (Smoke Stop) | 1/2 hour double | 2 hour double | no | 50 | 40 | 60 | 3 | 5 | 5
|  | Timber Glass | 1980 x 760 single safety glass panel | 1980 x 760 two safety glass panel | no | 50 | 40 | 60 | 3 | 3 | 3
| Interior Walls | Int Window - Metal | 10mm tough clear glazed screen, al frame | 10mm tough tinted glazed screen, al frame | m2 | 25 | 20 | 35 | 3 | 3 | 3
|  | Int Window - Timber | Timber framed glazed screen, 4mm clear | Timber framed glazed, 6mm toughened | m2 | 25 | 20 | 35 | 3 | 3 | 3
|  | Proprietary | Office partitions incl steel frame & gib | High spec partitions incl steel frame & gib - braced | m2 | 20 | 15 | 25 | 3 | 4 | 2
| Interior Windows | Alum/ Glass |  |  | m2 | 50 | 45 | 55 | 4 | 4 | 3
|  | Alum/ Safety glass |  |  | m2 | 50 | 45 | 55 | 4 | 5 | 5
|  | Lead glass |  |  | m2 | 50 | 45 | 55 | 4 | 4 | 3
|  | Safety glass |  |  | m2 | 50 | 45 | 55 | 4 | 5 | 5
| Wall Finishes | Fibrolite | 9.5mm - fibrous plaster | 19mm - fibrous plaster | m2 | 75 | 60 | 90 | 2 | 4 | 1
|  | Glass | Clear polycarbonate | Tinted polycarbonate | m2 | 50 | 40 | 60 | 4 | 3 | 2
|  | Gyprock Lining |  |  | m2 | 45 | 35 | 55 | 2 | 3 | 1
|  | Hardboard | 3mm hardboard | 6mm hardboard | m2 | 35 | 30 | 40 | 3 | 4 | 1
|  | Melteca / Seratone | Seratone | 6mm thick Hardiglaze Premium | m2 | 50 | 40 | 60 | 3 | 4 | 2
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 10 | 8 | 12 | 3 | 2 | 1
|  | Particle Board | Kopine Ultralock | Pynefloor Gold | m2 | 75 | 60 | 90 | 2 | 3 | 1
|  | Plaster Finish | Hardwall | Tyrolean | m2 | 45 | 35 | 55 | 4 | 4 | 1
|  | Plywood | 7 thick plywood | 21 thick plywood | m2 | 75 | 60 | 90 | 3 | 3 | 1
|  | Prefinished Metal |  |  | m2 | 40 | 35 | 50 | 4 | 3 | 3
|  | Stainless steel |  |  | m2 | 40 | 35 | 50 | 4 | 3 | 3
|  | Tiles - Ceramic | 150 x 150 ceramic | 200 x 100 ceramic | m2 | 50 | 40 | 60 | 4 | 4 | 4
|  | Timber Lining | T & G pine | Shiplap panelling | m2 | 65 | 50 | 80 | 2 | 3 | 1
|  | Vinyl | 2 thick standard sheet | 5.5 thick non slip sports | m2 | 20 | 18 | 24 | 3 | 3 | 3
|  | Wallpaper Finish | PC $30 a roll | Imported vinyl fabric pc $17/m2 | m2 | 11 | 9 | 16 | 4 | 4 | 1
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Lifts / Hoist Services | Vertical Transport | Car Interior & buttons | Basic spec, small car | High spec, large car | no | 18 | 15 | 20 | 4 | 4 | 2
|  | Car Structure |  |  | no | 38 | 30 | 45 | 1 | 3 | 3
|  | Door sets | Door operator and landing sets, low spec | Door operator and landing sets, high spec | no | 25 | 20 | 30 | 4 | 5 | 4
|  | Lift controller |  |  | no | 22 | 18 | 25 | 2 | 5 | 3
|  | Motor / Gears | Motor, up to 10Kw | Motor, over 10Kw | no | 15 | 12 | 18 | 1 | 4 | 2
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Mechanical Services | Air Distribution | Ducting |  |  | sum | 50 | 40 | 60 | 1 | 3 | 3
|  | Fire & Smoke Dampers |  |  | no | 18 | 15 | 20 | 1 | 4 | 5
|  | Hepa Filters |  |  | no | 4 | 3 | 5 | 1 | 5 | 5
|  | Supply Fans |  |  | no | 11 | 7 | 15 | 1 | 4 | 3
|  | Variable Air Volume |  |  | no | 15 | 10 | 20 | 1 | 4 | 4
| Air Handling Units | AHU - Motor |  |  | no | 15 | 10 | 20 | 1 | 3 | 3
|  | AHU Structure |  |  | no | 35 | 30 | 40 | 1 | 2 | 2
|  | Duct Heaters |  |  | no | 8 | 5 | 10 | 1 | 3 | 3
|  | Motorised valves |  |  | no | 8 | 5 | 10 | 1 | 3 | 2
|  | Variable Speed Drives |  |  | no | 8 | 5 | 10 | 1 | 4 | 4
| Building Management System | Cabling / mech / elect |  |  | sum | 43 | 35 | 50 | 1 | 3 | 1
|  | Computer /printer |  |  | no | 18 | 15 | 20 | 1 | 3 | 2
|  | Controller / hard drive |  |  | no | 18 | 15 | 20 | 1 | 3 | 3
| Chilled Water System | Chiller - Compressor |  |  | no | 11 | 10 | 13 | 1 | 3 | 3
|  | Chiller Structure |  |  | no | 33 | 25 | 40 | 1 | 3 | 1
|  | Pipework | Fire_Pipework_25 dia, screw fittings | Fire_Pipework_150 dia, grooved end joints & fittings | sum | 70 | 60 | 80 | 1 | 3 | 1
|  | Pumps |  |  | no | 12 | 9 | 15 | 1 | 3 | 3
|  | Valves |  |  | sum | 50 | 40 | 60 | 1 | 3 | 2
| Compressed Air/Pneumatics | Controller / Cabling |  |  | sum | 43 | 35 | 50 | 1 | 3 | 2
|  | Dryers |  |  | no | 11 | 7 | 15 | 1 | 4 | 3
|  | Engine |  |  | no | 25 | 20 | 30 | 1 | 4 | 3
|  | Pipe work |  |  | sum | 43 | 35 | 50 | 1 | 2 | 1
|  | Pneumatic valve actuators |  |  | no | 18 | 15 | 20 | 1 | 4 | 3
| Condenser Water System | Condensing Unit |  |  | no | 18 | 14 | 22 | 1 | 4 | 3
|  | Cooling tower - infills |  |  | no | 8 | 6 | 10 | 1 | 4 | 3
|  | Cooling tower - structure |  |  | no | 33 | 25 | 40 | 2 | 3 | 1
|  | Fans/Motors |  |  | no | 15 | 10 | 20 | 1 | 4 | 2
|  | Pipework | Fire_Pipework_25 dia, screw fittings | Fire_Pipework_150 dia, grooved end joints & fittings | sum | 70 | 60 | 80 | 1 | 2 | 1
|  | Pumps |  |  | no | 12 | 9 | 15 | 1 | 3 | 2
|  | Valves |  |  | no | 50 | 40 | 60 | 1 | 3 | 2
|  | Water tank |  |  | no | 40 | 30 | 50 | 1 | 2 | 1
| Fan Coil Units | Fan Coil Unit |  |  | no | 25 | 20 | 30 | 1 | 4 | 4
| Heating System | Boiler - gas fired |  |  | no | 28 | 20 | 35 | 2 | 4 | 4
|  | Burner |  |  | no | 25 | 20 | 30 | 3 | 4 | 4
|  | Hot Water Cylinder | Elect.disconnect,remove,low p. 70litre, | Elect. disconnect,remove,mains p. 270 litre, | no | 25 | 20 | 30 | 3 | 5 | 1
|  | Hot water pumps |  |  | no | 13 | 10 | 15 | 1 | 4 | 3
|  | Pipework | Fire_Pipework_25 dia, screw fittings | Fire_Pipework_150 dia, grooved end joints & fittings | sum | 70 | 60 | 80 | 1 | 2 | 1
|  | Space Heaters | Infra red strip heater, 1100W | Panel heater, 2000W wall mounted | no | 25 | 20 | 30 | 4 | 4 | 1
|  | Underflr/Wall &/Or Ceiling Heat. | Electric | Water fed | m2 | 35 | 30 | 50 | 1 | 4 | 3
|  | Valves |  |  | no | 50 | 40 | 60 | 1 | 3 | 2
| HVAC Control System | HVAC Control System |  |  | sum | 43 | 35 | 50 | 3 | 3 | 4
| Split A/C Units | Split A/C Units |  |  | no | 9 | 7 | 10 | 3 | 4 | 4
| Ventilation System | Axial Ventillation Fans | 315mm dia, 500l/sec @40Pa | 1000mm dia, 10,000l/sec @400Pa | no | 20 | 5 | 30 | 3 | 3 | 3
|  | Centrifugal Ventilation Fans | Single Width Single Inlet, 2300/500 | Double WidthDouble Inlet, 20000/1500 | no | 15 | 5 | 20 | 3 | 3 | 3
|  | Exhaust Fan |  |  | no | 15 | 13 | 18 | 3 | 3 | 1
|  | Ventilation System |  |  | sum | 43 | 35 | 50 | 3 | 3 | 4
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Plumbing | Sanitary Plumbing | Back Flow Valve |  |  | no | 15 | 12 | 20 | 1 | 3 | 3
|  | Bath | acrylic1525 long,2 taps, minor carpentry work | acrylic 1800 long,2 taps, minor carpentry work | no | 40 | 30 | 45 | 4 | 4 | 4
|  | Handbasin | wall mount&brackets,acrylic, 2 taps,connex | wall mount&brackets,vit china, 2 taps,connex | no | 40 | 30 | 45 | 4 | 4 | 1
|  | Laundry Tub | Stainless Steel ,brackets,2 taps,connex | Twin steel,brackets,2 taps,timber cabinet | no | 50 | 40 | 60 | 3 | 3 | 3
|  | Safety Shower and Eyewash unit |  |  | no | 25 | 20 | 30 | 4 | 3 | 3
|  | Shower Unit (Acrylic 3 Sided) | base&waste, line 3 sides,curtain,mixer & rose | tiled foor & walls & glass enclosure | no | 25 | 20 | 30 | 4 | 4 | 1
|  | Tap | Generic basin tap or Faucet | Methven Classical Nilo NL92 basin faucet | no | 20 | 16 | 24 | 3 | 4 | 3
|  | Toilet - China Bowl /Cistern | Vit. China,plastic seat&cistrn.cistrn tap | Caroma Walvit wc suite&water wafer inwall cist, cistern tap | no | 35 | 30 | 45 | 3 | 4 | 3
|  | Toilet - S/S Urinal | 5 litre ss cistern. 900 long SS slab urinal. Push button | 28 litre ss cistern.ss slab urinal, trap, tread, 1800mm, water saver IR sensor | no | 50 | 40 | 70 | 3 | 4 | 3
|  | Toilet Bowl & Cistern | Vit. China,plastic seat&cistrn.cistrn tap | Caroma Walvit wc suite&water wafer inwall cist, cistern tap | no | 35 | 30 | 45 | 3 | 4 | 1
|  | Urinal | 5 litre steel cistern & china wall hung | 28 litre ss cistern.Vitrous china wall hung urinal, trap | no | 35 | 30 | 45 | 3 | 4 | 1
|  | Vanity (Incl Basin) | 750 long completely melamine | 1500 long timber veneer | no | 40 | 30 | 45 | 4 | 4 | 1
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Security Services | Access Control Systems | Cabling |  |  | sum | 43 | 35 | 50 | 3 | 3 | 3
|  | Card readers / Keypad | Proximity reader | Card reader | sum | 10 | 8 | 12 | 3 | 4 | 3
|  | Controller Computer/badge printer etc |  |  | no | 13 | 10 | 15 | 3 | 3 | 3
| CCTV Systems | Cabling |  |  | sum | 43 | 35 | 50 | 1 | 2 | 3
|  | Cameras | Fixed lens internal | Zoom lens low light external | sum | 13 | 10 | 15 | 3 | 4 | 4
|  | Controller / hard drive |  |  | no | 18 | 15 | 20 | 1 | 4 | 4
|  | Monitors |  |  | no | 18 | 15 | 20 | 3 | 4 | 4
| Intruder/Duress Alarm System | Cabling |  |  | sum | 43 | 35 | 50 | 1 | 2 | 4
|  | Controller / hard drive |  |  | no | 18 | 15 | 20 | 1 | 4 | 4
|  | Monitors |  |  | no | 18 | 15 | 20 | 3 | 4 | 4
|  | Sensors |  |  | no | 13 | 10 | 15 | 3 | 4 | 4
| Special Services | Barrier Arms | Typical arms | Additional features | no | 20 | 16 | 24 | 4 | 5 | 4
|  | Card Reader | Proximity reader | Card reader | no | 20 | 16 | 24 | 3 | 5 | 5
|  | CCTV Camera / Monitor | Fixed lens internal | Zoom lens low light external | no | 7 | 6 | 9 | 4 | 5 | 5
|  | Elect. Security Sys. - Domestic | Basic | Additional detection | no | 15 | 12 | 18 | 3 | 5 | 5
|  | Generators (Standby) | 7 kVA | 100 kVA | no | 25 | 20 | 30 | 2 | 5 | 5
Component Group | Component Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | Useful Lives |  |  | Criticality
[6 empty] | Base | Lower | Upper | Appearance | Failure | Safety
Water Services | Domestic Cold Water | Dosing | Pump, dose metering, 1-5Ltr/hr | Pump, dose metering, 35Ltr/hr | sum | 13 | 10 | 15 | 1 | 5 | 5
|  | Tanks- Pipes |  |  | sum | 40 | 30 | 50 | 1 | 2 | 3
|  | Valves | Bronze Gate Valve, 25mm dia | Cast Iron Globe Valve, 150mm dia | sum | 25 | 20 | 30 | 1 | 3 | 3
| Domestic Hot Water | Circulation Pumps |  |  | no | 13 | 10 | 15 | 1 | 3 | 5
|  | Tanks- Pipes |  |  | sum | 40 | 30 | 50 | 1 | 2 | 2
|  | Treament |  |  | sum | 13 | 10 | 15 | 1 | 3 | 3
|  | Valves | Bronze Gate Valve, 25mm dia | Cast Iron Globe Valve, 150mm dia | sum | 9 | 8 | 10 | 1 | 3 | 3
|  | Water Cylinder | Elect.disconnect,remove,low p. 70litre, | Elect. disconnect,remove,mains p. 270 litre, | no | 14 | 12 | 15 | 2 | 3 | 3
| Warm Water | Dosing |  |  | no | 20 | 16 | 24 | 1 | 3 | 3
|  | HWS systems/controls |  |  | sum | 18 | 15 | 20 | 2 | 3 | 1
|  | Pipes and valves |  |  | sum | 50 | 40 | 60 | 1 | 2 | 3
|  | Pumps | 2 litre/sec @ 2m head | 30 litre/sec @ 18m head | no | 12 | 9 | 15 | 2 | 3 | 3

## BCG 2009 Nz
|  |  | Unit Rates for Gross Replacement Costs (GRC) | [7 empty] | Asset Information | [5 empty] | Low and High Unit Replacement Costs for NZ 2007
[17 empty] | Auckland |  | Wellington |  | Christchurch |  | Dunedin
Group | Type | Component | Description of 'Low rates' | Description of 'High rates' | Unit ID | 2006 Vrs1 Typical Rate | 2006 Vrs2 Typical Rate | 2007 Typical Rate | GRC 2007 |  | Useful Lives |  |  | Criticality
[9 empty] | Low | High | Low | Std | High | CoF | H&S | A | Low | High | Low | High | Low | High | Low | High
Exterior Wks, Sundries | Ext Wks - Access | Asphalt /Sealed Areas | 2 cts bitumen and metal chip surfacing | 250 basecourse,40thick asphalt | m2 | 30 | 30 | 30 | 8.4 | 50 | 8 | 10 | 12 | 3 | 3 | 4 | 10 | 65 | 10 | 60 | 10 | 60 | 10 | 60
|  | Carpark marking | Typical application | Typical application | m | 3 | 3.25 | 4 | 2 | 5 | 4 | 5 | 6 | 2 | 4 | 4 | 3.5 | 0 | 3.5 | 0 | 3.5 | 0 | 3.5 | 0
|  | Concrete Slab | 75 thick conc unreinforced | 125 conc on 250 hardfill, reinf, edge thickening | m2 | 65 | 77.536 | 80.5848 | 40.59 | 105.3642 | 40 | 50 | 60 | 3 | 3 | 3 | 55 | 155 | 55 | 150 | 50 | 135 | 55 | 145
|  | Kerb & Channelling | 75 wide kerb, 300 wide channel | kerb and channel, 250 x 300 wide | m | 42 | 47.0811 | 63 | 55 | 70 | 40 | 50 | 60 | 3 | 3 | 3 | 60 | 70 | 55 | 70 | 55 | 70 | 55 | 70
|  | Metal (Loose) | Crush rock in consolidated layers | 250 basecouse,2 coat chip | m2 | 8 | 8 | 23 | 15 | 30 | 4 | 5 | 6 | 2 | 2 | 1 | 20 | 30 | 20 | 20 | 15 | 15 | 20 | 20
|  | Timber Kerbs | Base parking barrier | Heavy duty barrier | m | 145 | 145 | 145 | 60 | 200 | 20 | 25 | 30 | 2 | 2 | 2 | 90 | 155 | 75 | 155 | 75 | 155 | 70 | 155
| Ext Wks - Grounds | Carport | Conc slab,timber frm, galv steel roof (kitset) | Higher quality including Colour steel | m2 | 220 | 257.1079 | 406 | 385 | 430 | 40 | 50 | 60 | 3 | 4 | 2 | 385 | 430 | 385 | 430 | 385 | 430 | 380 | 425
|  | Channels & Grating | P'cast channel 225wide& 50 th.grate | P'cast channel 450wide& 75 th.grate | m | 310 | 310 | 310 | 276 | 460 | 28 | 35 | 42 | 3 | 3 | 2 | 115 | 390 | 115 | 390 | 115 | 390 | 115 | 390
|  | Garage | 6x3.5m Conc, timber frame, galv steel clad | Ditto, brick veneer, conc tile roof | m2 | 670 | 786.8074 | 832.2759 | 554.6611 | 942.5811 | 40 | 50 | 60 | 3 | 4 | 3 | 690 | 1150 | 655 | 1105 | 635 | 1120 | 640 | 1105
|  | Letter Boxes | Steel proprietory | Timber with three parcel areas on conc base | no | 150 | 150 | 169.4444 | 120 | 377.7778 | 20 | 25 | 30 | 1 | 2 | 3 | 110 | 340 | 110 | 340 | 110 | 340 | 110 | 340
|  | Paint | Paint to ext walls, incl prep. 2 coat acrylic | waterblast surface, textured finish | m2 | 25 | 25 | 25 | 10 | 45 | 8 | 10 | 14 | 1 | 1 | 3 | 10 | 45 | 10 | 45 | 10 | 45 | 10 | 45
|  | Park Seat | 1.3m tubular frame with perforated steel top | 4 seat tubular frame with perforated steel top | no | 800 | 669.2063 | 750 | 500 | 1370 | 12 | 15 | 18 | 2 | 2 | 3 | 500 | 1370 | 500 | 1370 | 500 | 1370 | 500 | 1370
|  | Picnic Table | 2.1m tubular frame with perforated steel top | Timber seat and table | no | 650 | 966.4881 | 990 | 610 | 1370 | 12 | 15 | 18 | 2 | 2 | 3 | 610 | 1370 | 610 | 1370 | 610 | 1370 | 610 | 1370
|  | Rubbish Bin | Semi circular wall mounted | 52 litre stainless steel | no | 400 | 399.3827 | 480 | 400 | 560 | 12 | 15 | 18 | 3 | 4 | 3 | 405 | 560 | 405 | 560 | 405 | 560 | 400 | 560
|  | Shade Cloth | Woven nylon in green excluding frame | Woven nylon in white excluding frame | m2 | 14 | 14 | 13 | 10 | 15 | 14 | 15 | 16 | 4 | 4 | 3 | 10 | 15 | 10 | 15 | 10 | 15 | 10 | 15
|  | Shed ( Garden / Tool Shed ) | kitset on conc slab | Ditto, brick veneer, conc tile roof | no | 1200 | 1305.9921 | 3040 | 2230 | 3850 | 28 | 35 | 42 | 2 | 2 | 1 | 2230 | 3850 | 2230 | 3850 | 2230 | 3850 | 2230 | 3850
| Ext Wks - Paving | Asphalt Paths | 20 thick asphalt | 40 thick asphalt | m2 | 35 | 35 | 35 | 20.4 | 50 | 8 | 10 | 12 | 4 | 3 | 3 | 30 | 45 | 30 | 45 | 30 | 45 | 30 | 45
|  | Astro Turf | synthetic turf | sportsflex sports flooring | m2 | 90 | 90 | 90 | 42 | 120 | 8 | 10 | 12 | 2 | 1 | 4 | 70 | 245 | 70 | 245 | 70 | 245 | 70 | 245
|  | Cobblestone | 45 thick | 60 thick (23m2) with 100 thick basecourse | m2 | 70 | 80.9562 | 94 | 80 | 110 | 20 | 25 | 30 | 4 | 3 | 4 | 80 | 105 | 85 | 110 | 85 | 110 | 80 | 100
|  | Concrete Paths / Ramps | 150 thick path | 200 thick path 100 thick subbase | m2 | 90 | 113.7119 | 126 | 105 | 150 | 40 | 50 | 60 | 4 | 4 | 3 | 115 | 150 | 110 | 145 | 105 | 135 | 110 | 140
|  | Concrete Paver / Interlocking Blocks | 300 x 300 x 40 paving | 80mm conc brick pav,on 250 basecourse | m2 | 65 | 73.5347 | 115 | 105 | 125 | 40 | 50 | 60 | 4 | 3 | 3 | 110 | 125 | 110 | 125 | 105 | 120 | 105 | 120
| Ext Wks - Signs | Sign (Exterior) | Sign, exterior, building signage, basic | Sign, exterior, building signage, high quality | no | 2700 | 2700 | 2700 | 2160 | 2970 | 8 | 10 | 12 | 4 | 2 | 5 | 2700 | 27000 | 2700 | 27000 | 2700 | 27000 | 2700 | 27000
|  | Sign (Route) | Sign, exterior, route/direction, basic | Sign, exterior, route/direction, high quality | no | 400 | 400 | 400 | 135 | 675 | 8 | 10 | 12 | 4 | 2 | 5 | 135 | 675 | 135 | 675 | 135 | 675 | 135 | 675
|  | Sign (Timber) | Sign, interior, route/direction, basic | Sign, interior, route/direction, high quality | no | 250 | 250 | 250 | 110 | 550 | 8 | 10 | 12 | 4 | 2 | 5 | 110 | 540 | 110 | 540 | 110 | 540 | 110 | 540
Exterior Wks, Sundries | Fences | Block Wall | 150 block, footing no finish | 250 block, footing, no finish | m2 | 200 | 210.4733 | 442 | 395 | 490 | 60 | 75 | 90 | 3 | 3 | 3 | 425 | 490 | 415 | 470 | 395 | 450 | 415 | 475
|  | Brick Wall | 100 thick | 200 thick | m2 | 175 | 184.7144 | 184.7144 | 162 | 265 | 40 | 50 | 60 | 3 | 3 | 3 | 165 | 350 | 170 | 400 | 160 | 360 | 160 | 355
|  | Corrugated Iron Fence | .4 thick corrugated steel | .4 thick corrugated steel and timber frame | m2 | 40 | 32.0779 | 72 | 55 | 90 | 20 | 25 | 35 | 2 | 2 | 2 | 55 | 90 | 55 | 90 | 55 | 90 | 55 | 90
|  | Fence - Paint Finish | prep and one coat acrylic one side | prep and 3 coat enamel one side | m2 | 12 | 13.2 | 18 | 5 | 30 | 8 | 10 | 12 | 1 | 1 | 2 | 10 | 30 | 5 | 30 | 5 | 30 | 5 | 30
|  | Picket Fence | 1400 high timber | metal 1400 high, galv welded fence panels | m | 65 | 67.1489 | 235 | 155 | 315 | 20 | 25 | 35 | 2 | 2 | 2 | 155 | 315 | 155 | 315 | 155 | 315 | 155 | 315
|  | Post & Rail Fence | 1500 high, 150 x 19 timber paling | 1800 high, 150x 25 timber palings | m | 90 | 94.0909 | 122 | 120 | 125 | 20 | 25 | 35 | 2 | 2 | 2 | 120 | 125 | 120 | 125 | 120 | 125 | 120 | 125
|  | Post & Wire Fence | 7 wire and posts | 8 wire posts, battens | m | 55 | 65 | 48 | 35 | 60 | 28 | 35 | 42 | 2 | 2 | 2 | 35 | 60 | 35 | 60 | 35 | 60 | 35 | 60
|  | Post / Rail / Mesh Fence | 1800 high galv mesh | 2700 high, pvc coating, top rail, mowing strip | m | 65 | 66.3542 | 66.3542 | 37.2 | 68 | 20 | 25 | 35 | 2 | 2 | 2 | 35 | 95 | 35 | 95 | 40 | 95 | 40 | 95
|  | Retaining Walls (concrete) | 600 max ret, Grip block precast interlocking | 7400 max ret, Grip block precast interlocking | m2 | 330 | 330 | 330 | 210 | 480 | 60 | 75 | 90 | 5 | 4 | 3 | 180 | 580 | 180 | 580 | 190 | 605 | 190 | 605
|  | Retaining Walls (timber) | 1800 max retaining, Timbercrib | 6300 max retaining, Timbercrib | m2 | 390 | 390 | 390 | 216 | 507 | 40 | 50 | 60 | 5 | 4 | 3 | 195 | 475 | 185 | 460 | 200 | 495 | 205 | 505
|  | Timber Paling Fence | 1500 high 150 x 19 pailings | 1800 high 150 x 25 palings | m | 70 | 73.1818 | 122 | 120 | 125 | 20 | 25 | 35 | 2 | 2 | 2 | 120 | 125 | 120 | 125 | 120 | 125 | 120 | 125
|  | Wire Mesh Fence | Replace wire mesh only | Replace wire mesh only | m2 | 16 | 16 | 16 | 12 | 20 | 20 | 25 | 35 | 2 | 2 | 2 | 10 | 25 | 10 | 25 | 10 | 25 | 10 | 25
| Gates | Metal Gate | Metal Gate |  | no | 800 | 800 | 800 | 500 | 2500 | 40 | 50 | 60 | 3 | 2 | 2 | 500 | 2500 | 500 | 2500 | 500 | 2500 | 500 | 2500
|  | Motorised Sliding Gate | Single metal gate with motor and key pad | Double metal gate with motoe and key pad | no | 6000 | 6000 | 20000 | 16200 | 33750 | 20 | 25 | 30 | 3 | 3 | 4 | 16200 | 33750 | 16200 | 33750 | 16200 | 33750 | 16200 | 33750
|  | Steel/Mesh Gate | 1000 x 1800 high single | 4800 x 1800 high double | no | 650 | 650 | 650 | 264 | 720 | 20 | 25 | 35 | 3 | 2 | 3 | 260 | 805 | 260 | 805 | 265 | 810 | 265 | 810
|  | Timber Gate | Rough sawn single gate 1500 x 1800 high | Double T & G ornate timber gate | no | 500 | 500 | 500 | 240 | 2500 | 20 | 25 | 30 | 2 | 2 | 3 | 340 | 6750 | 340 | 6750 | 340 | 6750 | 340 | 6750
|  | Wrought Iron Gate | Standard single gate | Ornate double gate | no | 1200 | 1200 | 1200 | 480 | 3000 | 40 | 50 | 60 | 2 | 2 | 4 | 540 | 3375 | 540 | 3375 | 540 | 3375 | 540 | 3375
| Misc | Covered Ways | .4mm Endura corrugated | .9mm aluminium trough 300 profile | m2 | 260 | 299.8682 | 504 | 445 | 575 | 40 | 50 | 60 | 4 | 3 | 3 | 465 | 575 | 445 | 545 | 445 | 560 | 450 | 545
|  | Decking | Pine decking | Hardwood decking | m2 | 100 | 99.2188 | 102.8981 | 82.6667 | 124.9 | 40 | 50 | 60 | 4 | 4 | 3 | 80 | 125 | 80 | 125 | 75 | 135 | 80 | 130
|  | Sun Screen/Awning | Roll up awnings, canvas | Fixed awnings, canvas | ea | 300 | 349.2423 | 338.7657 | 273.6885 | 367.4227 | 24 | 30 | 36 | 4 | 4 | 4 | 305 | 485 | 345 | 305 | 305 | 485 | 305 | 485
|  | Verandah - Roof only | .4mm Endura corrugated | .9mm aluminium trough 400 profile | m2 | 110 | 89.1295 | 89.1295 | 54 | 130 | 40 | 50 | 60 | 4 | 3 | 3 | 50 | 145 | 50 | 145 | 50 | 145 | 50 | 145
| Tanks | Water Tank - Concrete | 4500 litre concrete water tank | 22700 litre concrete water tank | no | 3500 | 3921.5556 | 4412.66 | 2786.2859 | 6134.1285 | 40 | 50 | 60 | 4 | 4 | 1 | 2970 | 6210 | 2905 | 6280 | 3340 | 7425 | 3340 | 7425
|  | Water Tank - Metal | 9,000 litre galv steel water tank | 18,800 galv steel water tank | no | 4000 | 4000 | 4000 | 2295 | 7090 | 28 | 35 | 42 | 4 | 4 | 1 | 2295 | 7090 | 2295 | 7090 | 2295 | 7090 | 2295 | 7090
|  | Water Tank - Plastic | 135 litre | 5000 litre | no | 1500 | 1824.2225 | 1923.8522 | 335.5278 | 2923.3739 | 28 | 35 | 42 | 4 | 4 | 1 | 440 | 3310 | 425 | 3240 | 425 | 3240 | 425 | 3240
| Swimming Pools | Pool - Chemical Dosing Equip | Pool - Pump, dose metering, 1-5Ltr/hr | Pool - Pump, dose metering, 35Ltr/hr | no | 2500 | 2626.9368 | 2626.9368 | 975 | 4675 | 8 | 10 | 12 | 5 | 5 | 1 | 1025 | 4910 | 1025 | 4910 | 1025 | 4910 | 1025 | 4910
|  | Pool - Chemical Tanks | Chemical PE tank, 5,000 L | Chemical PE tank, 10,000 L | no | 4000 | 4199.839 | 4199.839 | 3105 | 5400 | 12 | 15 | 18 | 4 | 4 | 1 | 3260 | 5670 | 3260 | 5670 | 3260 | 5670 | 3260 | 5670
|  | Pool - Concrete Tank | PE Water tank, 5,000 litre | Concrete Tank, 5,000 gals | no | 3800 | 3988.3245 | 3988.3245 | 2025 | 4725 | 40 | 50 | 60 | 4 | 4 | 1 | 2125 | 4960 | 2125 | 4960 | 2125 | 4960 | 2125 | 4960
|  | Pool - Controls | Monitoring & control equip, ph/control only | Monitoring & control equip,chlorine, ph/control | no | 3300 | 3466.6603 | 3466.6603 | 1675 | 5770 | 8 | 10 | 14 | 4 | 3 | 2 | 1760 | 6060 | 1760 | 6060 | 1760 | 6060 | 1760 | 6060
|  | Pool - Filters | Pressure sand filter, 2.54m2 filter area | DE Vacuum, 1250m3 pool | no | 25000 | 26249.853 | 26249.853 | 23625 | 60750 | 20 | 25 | 30 | 5 | 5 | 1 | 24805 | 63790 | 24805 | 63790 | 24805 | 63790 | 24805 | 63790
|  | Pool - Heaters / Boilers | Heater, 125 MJ, gas | Heater, 400 MJ, gas | no | 6500 | 6827.1972 | 6827.1972 | 4860 | 9450 | 12 | 15 | 18 | 4 | 4 | 2 | 5105 | 9925 | 5105 | 9925 | 5105 | 9925 | 5105 | 9925
|  | Pool - Piping (PVC) | Pipe, 15mm, pvc, hi strength | Pipe, 200mm, cpvc, hi temp | m | 3000 | 3075.5556 | 3075.5556 | 30 | 3375 | 32 | 40 | 48 | 3 | 2 | 1 | 30 | 3545 | 30 | 3545 | 30 | 3545 | 30 | 3545
|  | Pool - Pumps | Pump, 5l/s at 12m | Pump, 20l/s at 20m | no | 3000 | 3150.2137 | 3150.2137 | 2700 | 8775 | 5.6 | 7 | 9 | 2 | 2 | 1 | 2835 | 9215 | 2835 | 9215 | 2835 | 9215 | 2835 | 9215
|  | Pool - Skimmers & Nozzles | Skimmer & Nozzle | Skimmer & Nozzle | no | 500 | 523.9198 | 523.9198 | 405 | 540 | 16 | 20 | 25 | 2 | 3 | 1 | 425 | 565 | 425 | 565 | 425 | 565 | 425 | 565
|  | Pool - Valve, 15mm | Valve, 15mm, ball, PVC, GF coloro | Valve, 15mm, ball, PVC, GF 346 | no | 350 | 359.4086 | 359.4086 | 35 | 930 | 8 | 10 | 12 | 3 | 3 | 1 | 35 | 980 | 35 | 980 | 35 | 980 | 35 | 980
|  | Pool - Valve, 300mm | 300mm, lugged b'fly, CI body, SS, manual | 300mm, lugged b'fly, CI body, SS, actuated | no | 3000 | 3148.6177 | 3148.6177 | 2430 | 4930 | 8 | 10 | 12 | 3 | 3 | 1 | 2550 | 5175 | 2550 | 5175 | 2550 | 5175 | 2550 | 5175
|  | Pool -Tiles | 150 ceramic tiles | Mosaic tiles | m2 | 155 | 155 | 159.7038 | 155.1265 | 163.75 | 16 | 20 | 25 | 5 | 5 | 5 | 155 | 175 | 155 | 160 | 155 | 160 | 155 | 160
External Fabric | External Stairs | Handrail metal | 45 dia aluminium wall mounted | 50 dia brass wall mounted | m | 120 | 142.2704 | 142.2704 | 60 | 200 | 40 | 50 | 60 | 5 | 5 | 4 | 95 | 290 | 95 | 290 | 95 | 290 | 95 | 290
|  | Handrail Timber | 100 x 50 pine wall mounted | 45 dia Rimu wall mounted | m | 45 | 45 | 107 | 100 | 115 | 40 | 50 | 60 | 5 | 5 | 4 | 100 | 115 | 100 | 115 | 100 | 115 | 100 | 115
|  | Staircase - Metal | 1000 wide straight | 1500 dia spiral stair | m/H | 1200 | 4500 | 4500 | 3600 | 4950 | 60 | 75 | 90 | 4 | 4 | 3 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500 | 4500
|  | Staircase - Timber | 900 wide pine | 1000 wide pine with balustrade one side | m/H | 800 | 901.4977 | 529 | 400 | 658 | 40 | 50 | 60 | 4 | 4 | 3 | 410 | 670 | 380 | 640 | 410 | 670 | 400 | 650
| External Walls | Aluminium | 1.6 thick | 1.6 thick and more difficult installation | m2 | 130 | 168.2699 | 153 | 130 | 175 | 60 | 75 | 90 | 3 | 2 | 4 | 130 | 175 | 130 | 175 | 130 | 175 | 130 | 175
|  | Brick Cladding | 70mm veneer Firth classic. No finish | 70mm veneer Monier cotswold. No finish | m2 | 150 | 163.5543 | 163.5543 | 145 | 175 | 60 | 75 | 90 | 3 | 2 | 4 | 140 | 180 | 160 | 180 | 135 | 170 | 145 | 170
|  | Curtain Walling (Glass) | Alum. 50% clear glass 50% armourclad | more difficult installation | m2 | 830 | 1034.8083 | 1003 | 890 | 1115 | 45 | 55 | 75 | 3 | 3 | 5 | 890 | 1115 | 890 | 1115 | 890 | 1115 | 890 | 1115
|  | Fibrolite Sheeting | Hardiflex | Titan 9mm wall board, primed, epoxied, jointed, battens behind | m2 | 80 | 120 | 119.9272 | 69.9777 | 195 | 40 | 50 | 65 | 3 | 2 | 3 | 70 | 195 | 70 | 190 | 70 | 190 | 75 | 190
|  | Hardiplank | 240 smooth | 240 vertical and 180 under | m2 | 90 | 107.6463 | 114.9124 | 87.3438 | 127.2 | 40 | 50 | 60 | 3 | 2 | 4 | 105 | 130 | 105 | 130 | 110 | 135 | 110 | 135
|  | Marble | 300 x 300 x 10 tiles | 20 thick panels | m2 | 600 | 600 | 600 | 340 | 700 | 80 | 100 | 120 | 3 | 2 | 5 | 340 | 700 | 340 | 700 | 340 | 700 | 340 | 700
|  | Metal Cladding | .75 thick galv sheet | 1 mm thick electro galvanised | m2 | 70 | 80.1818 | 80.1818 | 60 | 90 | 40 | 50 | 60 | 3 | 2 | 3 | 60 | 90 | 60 | 90 | 60 | 90 | 60 | 90
|  | Paint Finish | Typical application of acrylic paint, seal and 2 coats | Enamel paint, seal and 2 coats & more difficult application | m2 | 18 | 19 | 19 | 17 | 22 | 8 | 10 | 12 | 2 | 1 | 4 | 18 | 23 | 17 | 22 | 17 | 22 | 17 | 22
|  | Plaster | 2 ct wood float | Tyrolean | m2 | 65 | 63.789 | 78.2227 | 56.4911 | 108.3189 | 40 | 50 | 60 | 3 | 2 | 4 | 62 | 86 | 60 | 84 | 58 | 80 | 58 | 80
|  | Plywood | 7 thick plywood | 21 thick plywood | m2 | 80 | 71.123 | 74.7449 | 55.4401 | 99.2461 | 45 | 50 | 75 | 3 | 2 | 3 | 60 | 110 | 56 | 102 | 56 | 100 | 58 | 106
|  | Precast Concrete Wall Panels | 125 thick | 200 thick | m2 | 300 | 327.6718 | 343.1547 | 248.7176 | 357.4647 | 80 | 100 | 150 | 4 | 2 | 4 | 265 | 370 | 250 | 365 | 235 | 315 | 245 | 380
|  | PVC Weatherboards | Certainteed rusticated | Palliside rusticated | m2 | 150 | 150 | 155.384 | 124.069 | 163.4659 | 30 | 35 | 40 | 3 | 2 | 3 | 155 | 175 | 155 | 170 | 155 | 170 | 155 | 170
|  | Shiplap | 200 x 25 cedar | 150 x 25 cedar | m2 | 210 | 229.7343 | 216 | 205.0223 | 226.25 | 60 | 75 | 90 | 3 | 2 | 3 | 205 | 230 | 205 | 225 | 205 | 225 | 205 | 225
|  | Weatherboard - Timber | 150 x 25 pine | 200 x 25 cedar | m2 | 185 | 185 | 188.8562 | 180.9933 | 211.25 | 60 | 75 | 90 | 3 | 2 | 4 | 195 | 215 | 190 | 210 | 180 | 210 | 180 | 210
| Roof | Butynol Roofing | 1 thick black incl replace plywood | 1.5 thick grey including replace plywood | m2 | 130 | 134.7453 | 138.3676 | 123.9411 | 162.0362 | 16 | 20 | 24 | 5 | 2 | 1 | 128.925 | 170.1 | 120 | 160 | 120 | 155 | 125 | 160
|  | Colour Steel | 0.4mm Endura Corrugate | 0.55mm ZRX Dimondek 400 trough | m2 | 80 | 76.362 | 76.362 | 64 | 126.5 | 15 | 30 | 45 | 4 | 2 | 3 | 64 | 128 | 64 | 126 | 64 | 126 | 64 | 126
|  | Compressed Fibre | 9mm thick Hardipanel | 18mm thick Hardipanel | m2 | 130 | 130.3327 | 122.3155 | 101.1185 | 201.3403 | 40 | 50 | 65 | 4 | 2 | 2 | 100 | 195 | 100 | 200 | 100 | 205 | 100 | 210
|  | Concrete Roof Slabs | 75 thick | 150 thick | m2 | 270 | 247.7994 | 256.5837 | 227.5245 | 260.8408 | 75 | 100 | 150 | 4 | 2 | 1 | 230 | 265 | 225 | 255 | 215 | 240 | 225 | 255
|  | Decramastic | Decrabond to 30 degree pitch | Decrabond to 46 degree pitch and over | m2 | 65 | 65 | 65 | 60 | 70 | 25 | 35 | 45 | 4 | 2 | 3 | 60 | 70 | 60 | 70 | 60 | 70 | 60 | 70
|  | Downpipes - Metal | 65 dia zincalume steel | 100 dia S.S. | m | 36 | 66.2059 | 66.2059 | 58 | 142 | 25 | 35 | 45 | 2 | 1 | 2 | 58 | 142 | 58 | 142 | 58 | 142 | 58 | 142
|  | Downpipes - PVC | 65 dia PVC | 100 dia PVC | m | 28 | 40.938 | 49 | 40.0481 | 58.0287 | 25 | 35 | 40 | 2 | 1 | 2 | 40 | 58 | 40 | 58 | 40 | 58 | 40 | 58
|  | Glass | Clear polycarbonate | Tinted polycarbonate | m2 | 50 | 46.9351 | 46.9351 | 45.1172 | 55 | 40 | 50 | 60 | 3 | 3 | 4 | 45 | 55 | 45 | 55 | 45 | 55 | 45 | 55
|  | Metal Roofing | 0.4mm zincalume corrugated | .9mm aluminium trough 400 profile | m2 | 70 | 56.6797 | 56.6797 | 45 | 156.25 | 20 | 25 | 30 | 4 | 2 | 3 | 45 | 160 | 45 | 155 | 45 | 155 | 45 | 155
|  | Paint Finish | Acrylic paint to corrugated surface, for single storey limited scaffolding | Acrylic paint to trough section 300 & working at height and difficult application | m2 | 18 | 19 | 19 | 17 | 22 | 8 | 10 | 14 | 2 | 1 | 3 | 24 | 28 | 24 | 38 | 24 | 38 | 24 | 38
|  | Shingles - Timber | Treated pine shingles | Cedar shingles more difficult installation | m2 | 120 | 131.5385 | 131.5385 | 96 | 155 | 30 | 35 | 42 | 4 | 2 | 4 | 120 | 155 | 120 | 155 | 120 | 155 | 120 | 155
|  | Skylight | 610sq Adlux low profile spandrome nonvent. | 2075 x 2075 Adlux pyramid spandome | m2 | 2250 | 2250 | 2250 | 540 | 3140 | 40 | 50 | 60 | 4 | 4 | 3 | 540 | 2835 | 540 | 3040 | 540 | 3240 | 540 | 3445
|  | Soffits - Fibrolite | Hardiflex, 4.5mmPVC mouldings | Silkline Prefinished Soffit Linings & Working at height | m2 | 60 | 69.65 | 72.969 | 63.5883 | 88.7939 | 40 | 50 | 60 | 1 | 1 | 2 | 58 | 94 | 58 | 92 | 58 | 96 | 58 | 96
|  | Soffits - Timber | 7 thick plywood | 12 thick pine | m2 | 95 | 101.2769 | 104.9679 | 59.7967 | 155.2455 | 40 | 50 | 60 | 1 | 1 | 3 | 60 | 156 | 56 | 152 | 56 | 152 | 58 | 152
|  | Spouting - Metal | 125 zincalume steel | 125 copper | m | 36 | 40.7828 | 40.7828 | 38.0262 | 86.0103 | 25 | 35 | 45 | 4 | 2 | 3 | 38 | 86 | 38 | 86 | 38 | 86 | 38 | 86
|  | Spouting - PVC | 125 dia PVC | Magnum 170mm half round gutter | m | 40 | 54.9625 | 54.9625 | 46.7 | 74.7475 | 25 | 35 | 40 | 4 | 2 | 2 | 46 | 64 | 44 | 62 | 44 | 62 | 44 | 62
|  | Tile Roofing - Clay | Portoghese clay tile | French profile clay tile | m2 | 115 | 115 | 115 | 110 | 135 | 40 | 50 | 60 | 4 | 2 | 3 | 110 | 135 | 110 | 135 | 110 | 135 | 110 | 135
|  | Tile Roofing - Concrete | Rosscrete hacienda to single storey | Monier to 3 storey | m2 | 66 | 66 | 60 | 45 | 80 | 60 | 75 | 90 | 4 | 2 | 2 | 50 | 60 | 45 | 80 | 45 | 65 | 45 | 80
|  | Tile Roofing - Slate | Resin bonded reconstituted slate | Welsh slate | m2 | 280 | 280 | 280 | 245 | 460 | 80 | 100 | 120 | 4 | 2 | 4 | 245 | 460 | 245 | 460 | 245 | 460 | 245 | 460
|  | Timber Fascia | 150 x 25 | 250 x 40 thick | m | 40 | 44.9583 | 46.6365 | 30 | 90.0917 | 40 | 50 | 60 | 3 | 1 | 3 | 30 | 100 | 30 | 85 | 30 | 85 | 30 | 85
|  | Translucent Sheeting | PVC sheeting | Duralite fibreglass | m2 | 45 | 44.7991 | 50 | 45 | 55 | 20 | 25 | 30 | 3 | 3 | 3 | 45 | 55 | 45 | 55 | 45 | 55 | 45 | 55
| Windows & Doors | Alum Frame Glass - Dble Door | 1980x1620 dble with 6 thick toughened glass | Larger doors, higher specification | no | 2770 | 3273.2341 | 3273.2341 | 2216 | 3780 | 40 | 50 | 60 | 4 | 3 | 3 | 3040 | 4785 | 3040 | 4785 | 3040 | 4785 | 3040 | 4785
|  | Alum Frame Glass - Sgle Door | 1980x810 single with 6 thick toughened glass | Larger doors, higher specification | no | 1755 | 1886.8217 | 2107.3612 | 1568 | 2490.8187 | 40 | 50 | 60 | 3 | 3 | 2 | 1960 | 2865 | 1960 | 2865 | 1960 | 2865 | 1960 | 2865
|  | Alum/Glass - Sliding Dble Door | 1980x1620 dble with 6 thick toughened glass | Larger doors, higher specification | no | 2300 | 2638.5721 | 2638.5721 | 2230 | 3175 | 40 | 50 | 60 | 4 | 3 | 3 | 2430 | 3825 | 2430 | 3825 | 2430 | 3825 | 2430 | 3825
|  | Alum/Glass - Sliding Sgle Door | 1980x810 sgle with 6 thick toughened glass | Larger doors, higher specification | no | 1400 | 1493.1953 | 1641.0083 | 1335 | 1857.6762 | 40 | 50 | 60 | 3 | 3 | 2 | 1335 | 2105 | 1335 | 2105 | 1335 | 2105 | 1335 | 2105
|  | Aluminium Windows | Single glazed | Double glazed | m2 | 425 | 486.0666 | 486.0666 | 340 | 650 | 40 | 50 | 60 | 4 | 3 | 3 | 465 | 715 | 465 | 715 | 465 | 715 | 465 | 715
|  | Automatic Opening Doors | Single glazed - elect. lock/beam/mat switch | 3leaf/bifolding - elect. lock/beam/mat switch | no | 8500 | 8507.2034 | 8507.2034 | 8100 | 11070 | 20 | 25 | 30 | 4 | 3 | 4 | 8100 | 10800 | 8100 | 10800 | 8100 | 10800 | 8100 | 11880
|  | Door Hardware (handles/locks) | basic lever style | High quality | no | 260 | 260 | 290.1766 | 170.0343 | 580 | 20 | 25 | 30 | 3 | 3 | 3 | 170 | 580 | 170 | 580 | 170 | 580 | 170 | 580
|  | Emergency Exit Door - Double | Standard style doors | Larger doors | no | 1800 | 1912.7164 | 1912.7164 | 1587.5 | 3892.5 | 40 | 50 | 60 | 5 | 5 | 4 | 1600 | 4405 | 1575 | 4360 | 1580 | 4365 | 1595 | 4390
|  | Emergency Exit Door - Single | Standard style door | Larger doors | no | 1250 | 1328.6633 | 1366.5421 | 1158.7558 | 1827.5 | 40 | 50 | 60 | 5 | 5 | 4 | 1170 | 2075 | 1150 | 2045 | 1155 | 2045 | 1160 | 2065
|  | Glass Door | Sgle 10mm tough. frameless glass doors | Larger doors | no | 8100 | 9000 | 9000 | 6480 | 10800 | 40 | 50 | 60 | 4 | 3 | 3 | 8100 | 12150 | 8100 | 12150 | 8100 | 12150 | 8100 | 12150
|  | Louvre Windows | 900 x 1000 timber frame fixed | 900 x 1000 timber frame adjustable | m2 | 370 | 382.3467 | 382.3467 | 296 | 400 | 30 | 35 | 45 | 2 | 2 | 2 | 370 | 400 | 370 | 400 | 370 | 400 | 370 | 400
|  | Metal Clad Doors | Zintec metal clad single door | Stainless steel clad single door | no | 615 | 478.4802 | 725 | 598 | 855 | 28 | 35 | 42 | 2 | 3 | 2 | 580 | 855 | 615 | 900 | 305 | 305 | 310 | 310
|  | Metal Framed Windows | Steel commercial over 0.5 m2 | Steel residential under 0.5 m2 | m2 | 815 | 921.089 | 921.089 | 810 | 1035 | 40 | 50 | 60 | 4 | 3 | 3 | 890 | 1135 | 890 | 1135 | 890 | 1135 | 890 | 1135
|  | Metal Roller Doors | Continuous curtain | Interlocking slat | m2 | 165 | 181.5984 | 181.5984 | 156.25 | 360 | 28 | 35 | 42 | 3 | 2 | 2 | 170 | 375 | 170 | 380 | 175 | 400 | 175 | 425
|  | Paint Finish | Enamel simple application | Enamel, colonial style glazed doors | m2 | 25 | 26.0417 | 26.0417 | 24 | 32 | 8 | 10 | 12 | 2 | 1 | 2 | 26 | 34 | 24 | 34 | 24 | 34 | 24 | 34
|  | Sliding Doors | Aluminium glazed single door | Larger door | no | 1400 | 1462.7803 | 1535.0163 | 1335 | 2230 | 40 | 50 | 60 | 3 | 3 | 3 | 1335 | 2430 | 1335 | 2430 | 1335 | 2430 | 1335 | 2430
|  | Timber Framed Windows | Pine | Cedar colonial | m2 | 800 | 833.4491 | 833.4491 | 795 | 930 | 40 | 50 | 60 | 4 | 3 | 4 | 810 | 945 | 810 | 945 | 810 | 945 | 810 | 945
|  | Timber / Glass Door | Half glass and half timber | 860mm x 40mm top and sidelight panels glazed | no | 1190 | 1190 | 1250 | 1190 | 1310 | 40 | 50 | 60 | 4 | 3 | 3 | 1190 | 1310 | 1190 | 1310 | 1190 | 1310 | 1190 | 1310
|  | Timber Entrance Door | Pine no finish incl frame | Fiji Kauri no finish incl frame | no | 900 | 900 | 900 | 778.75 | 1310 | 40 | 50 | 60 | 3 | 4 | 3 | 790 | 1325 | 765 | 1305 | 775 | 1295 | 785 | 1315
Interior Finishes | Ceiling Finishes | Fibrolite | 9.5mm - fibrous plaster | 19mm - fibrous plaster | m2 | 55 | 61.5152 | 60 | 52 | 68 | 60 | 75 | 90 | 3 | 1 | 3 | 52 | 72 | 52 | 64 | 52 | 66 | 50 | 68
|  | Gib-board Lining | 10 Gib | 16mm fire rated Gib board | m2 | 38 | 48.8133 | 51.0955 | 34 | 61.2364 | 40 | 50 | 60 | 3 | 1 | 4 | 42 | 62 | 42 | 64 | 42 | 64 | 42 | 68
|  | Hardboard | 3mm hardboard | 6mm hardboard | m2 | 30 | 35.0209 | 35.0209 | 26 | 45 | 60 | 75 | 90 | 3 | 1 | 3 | 28 | 48 | 28 | 48 | 28 | 50 | 28 | 50
|  | Insulation | Pink batts R1.8 | Thermofleece C2 | m2 | 18 | 18 | 19.2857 | 16 | 30 | 60 | 75 | 90 | 2 | 4 | 1 | 16 | 30 | 16 | 30 | 16 | 30 | 16 | 30
|  | Paint Finish | Two coats acrylic to plaster | Seal and 2 coats acrylic to Gib | m2 | 18 | 19 | 19 | 17 | 22 | 8 | 10 | 12 | 2 | 1 | 3 | 12 | 16 | 12 | 16 | 12 | 16 | 12 | 16
|  | Particle Board | Kopine Ultralock | Pynefloor Gold | m2 | 50 | 50.5884 | 51.0748 | 48 | 55.5481 | 60 | 75 | 90 | 3 | 1 | 3 | 50 | 54 | 48 | 52 | 50 | 52 | 52 | 54
|  | Plaster Finish | Hardwall | Tyrolean | m2 | 60 | 56 | 70.2593 | 52.3896 | 105.9725 | 40 | 50 | 60 | 3 | 1 | 3 | 58 | 84 | 56 | 82 | 54 | 76 | 54 | 76
|  | Softboard / Pinex Tiles / Lining | 13 thick wood fibre panels | 38 thick wood fibre panels, acoustic | m2 | 45 | 47.0905 | 47.0905 | 38 | 68.5 | 40 | 50 | 60 | 3 | 1 | 3 | 42 | 70 | 40 | 68 | 42 | 68 | 42 | 68
|  | Suspended Panel (incl Frame) | Exposed suspension system with fibrous plaster acoustic tiles | Concealed suspension system with tiles | m2 | 65 | 65 | 79.3555 | 68.4812 | 101 | 40 | 50 | 60 | 3 | 2 | 3 | 68 | 102 | 68 | 94 | 68 | 94 | 68 | 114
|  | Timber Lining | T & G pine | Shiplap panelling | m2 | 175 | 183.2111 | 166 | 150 | 181.6657 | 60 | 75 | 90 | 3 | 1 | 3 | 155 | 185 | 150 | 180 | 150 | 180 | 150 | 180
| Fixtures & Fittings | Fixed Desks, Tables, Seating | Workstation, medium quality | Workstation, high quality | no | 1650 | 1650 | 1650 | 945 | 2025 | 16 | 20 | 25 | 3 | 3 | 3 | 945 | 2025 | 945 | 2025 | 945 | 2025 | 945 | 2025
|  | Fixed Seating | Base timber seating | High specification seating | no | 210 | 150.4979 | 150.4979 | 100 | 190 | 16 | 20 | 25 | 3 | 3 | 2 | 100 | 190 | 100 | 190 | 100 | 190 | 100 | 190
|  | Handrail Stainless | 600mm long, 25mm dia, stainless steel | 750mm x 750mm, 32mm dia, stainless steel | ea | 200 | 200 | 216 | 150 | 290 | 20 | 25 | 40 | 4 | 5 | 3 | 150 | 290 | 150 | 290 | 150 | 290 | 150 | 290
|  | Hot Water Cylinder | Elect.disconnect,remove,low p. 70litre, | Elect. disconnect,remove,mains p. 270 litre, | no | 1400 | 1613.6829 | 1914.9225 | 1471.8934 | 3250.3555 | 20 | 25 | 30 | 5 | 4 | 1 | 1800 | 3355 | 1780 | 3330 | 1780 | 3330 | 1780 | 3330
|  | Internal Sign (Non-Illum) | Hardware_Sign_Engraved |  | no | 17 | 17 | 17 | 14 | 20 | 20 | 25 | 30 | 3 | 3 | 3 | 14 | 20 | 14 | 20 | 14 | 20 | 14 | 20
|  | Joinery Fttgs - Built-in | Painted MDF | Melamine carcass with solid Rimu fronts | m | 1050 | 1050 | 1049.8485 | 767.1259 | 1124.5475 | 32 | 40 | 48 | 3 | 3 | 3 | 930 | 1325 | 855 | 1220 | 675 | 1025 | 620 | 940
|  | Kitchen Bench S/S | Unpainted MDF with SS top | Melamine with solid Rimu fronts SS top | m | 1500 | 1510.6604 | 1608.2104 | 1341.1194 | 1968.3865 | 30 | 40 | 45 | 4 | 4 | 3 | 1510 | 2180 | 1425 | 2060 | 1245 | 1865 | 1190 | 1775
|  | Mirror | Clear float, 1m x 1m | 6 thick polycarbonate | ea | 260 | 260 | 260 | 255 | 290 | 16 | 20 | 30 | 3 | 2 | 2 | 255 | 290 | 255 | 290 | 255 | 290 | 255 | 290
|  | Paint Finish | To easy accessed timber surfaces | High quality enamel and difficult application | m2 | 25 | 26.0417 | 26.0417 | 24 | 32 | 8 | 10 | 12 | 3 | 1 | 3 | 14 | 26 | 14 | 24 | 14 | 24 | 14 | 24
|  | Shelving | Pine no finish | 18 thick melamine | m | 38 | 38 | 38 | 18 | 42 | 28 | 35 | 42 | 3 | 3 | 2 | 18 | 42 | 18 | 42 | 18 | 42 | 18 | 42
|  | Stoves | Average electric wall oven | De-lux gas wall oven | no | 1700 | 1900 | 1900 | 1655 | 7090 | 12 | 15 | 20 | 5 | 4 | 4 | 1655 | 7090 | 1655 | 7090 | 1655 | 7090 | 1655 | 7090
|  | Work Benches | Laminated top | Stainless Steel top | m | 410 | 410 | 420.2708 | 310 | 460 | 32 | 40 | 48 | 3 | 3 | 2 | 310 | 460 | 310 | 460 | 310 | 460 | 310 | 460
|  | Zip Heater | remove, 45 litre, elec connex | remove, 315 litre, elec connex | no | 2100 | 2500 | 2720.016 | 2148.6994 | 2891.5339 | 20 | 25 | 30 | 4 | 4 | 3 | 2585 | 3015 | 2655 | 3080 | 2350 | 2835 | 2350 | 2835
| Floor Finishes | Carpet | Nylon loop pile, direct stick | Heavy duty Axminster, double stick underlay | m2 | 95 | 95 | 95 | 40 | 185 | 12 | 15 | 22 | 4 | 4 | 4 | 40 | 185 | 40 | 185 | 40 | 185 | 40 | 185
|  | Ceramic tiles | Glazed quarry tiles, 300 x 300 | Ceramic mosaic tiles, 50mm x 50mm | m2 | 155 | 155 | 152 | 140 | 175 | 40 | 50 | 60 | 3 | 2 | 4 | 140 | 175 | 140 | 160 | 140 | 160 | 140 | 160
|  | Cork | Cork tiles, sanding, 3 coat polyurethane finish | Cork tiles, sanding, 4 coat poly | m2 | 95 | 95 | 112 | 95 | 130 | 20 | 25 | 30 | 3 | 3 | 4 | 95 | 130 | 95 | 130 | 95 | 130 | 95 | 130
|  | Floating timber | 7 mm veneer system | Solid timber (20 mm) | m2 | 120 | 135 | 172 | 135 | 210 | 10 | 15 | 30 | 4 | 3 | 4 | 135 | 210 | 135 | 210 | 135 | 210 | 135 | 210
|  | Floor - Particle Board | Kopine Ultralock | Premafloor purple tongue | m2 | 50 | 49.6843 | 50.9265 | 47.5 | 56.4375 | 60 | 75 | 90 | 3 | 3 | 3 | 50 | 55 | 50 | 50 | 50 | 50 | 50 | 55
|  | Floor - Timber T & G | Jarrah incl finish | Heart Rimu incl finish | m2 | 300 | 300 | 300 | 278.75 | 331.25 | 60 | 75 | 90 | 3 | 3 | 5 | 290 | 345 | 260 | 305 | 300 | 360 | 265 | 315
|  | Paint Finish | Prepare and paint | Concrete slab paint | m2 | 18 | 19 | 19 | 17 | 22 | 8 | 10 | 12 | 2 | 2 | 3 | 16 | 48 | 16 | 48 | 16 | 48 | 16 | 48
|  | Parquet | Boral Australian | NZ hardwoods | m2 | 200 | 200 | 204 | 190 | 210 | 40 | 50 | 60 | 4 | 3 | 4 | 190 | 195 | 205 | 210 | 205 | 210 | 205 | 210
|  | Polyurethane Finish | Three coats | Four coats | m2 | 25 | 25 | 28 | 24 | 32 | 8 | 10 | 12 | 3 | 2 | 3 | 24 | 32 | 24 | 32 | 24 | 32 | 24 | 32
|  | Rubber | 2 thick smooth for light traffic | 4 thick studded for heavy traffic | m2 | 95 | 95 | 112 | 95 | 130 | 28 | 35 | 42 | 3 | 3 | 2 | 95 | 130 | 95 | 130 | 95 | 130 | 95 | 130
|  | Stair Nosing | Standard for vinyl | Aluminium for carpet etc | m | 40 | 40 | 40 | 16 | 54 | 12 | 15 | 18 | 3 | 5 | 5 | 32 | 60 | 32 | 60 | 32 | 60 | 32 | 60
|  | Vinyl | 2 thick standard sheet | 5.5 thick non slip sports | m2 | 45 | 47.5 | 47.5 | 36 | 135 | 16 | 20 | 24 | 3 | 3 | 3 | 45 | 150 | 45 | 150 | 45 | 150 | 45 | 150
| Interior Doors | Accordion / Folding | Accordian doors | Larger doors | m2 | 395 | 395 | 395 | 305 | 405 | 16 | 20 | 24 | 3 | 2 | 3 | 305 | 405 | 305 | 405 | 305 | 405 | 305 | 405
|  | Door Closer | Cylindrical lockset, domestic qual | Mortice latchset, commercial quality | no | 270 | 270 | 300.8772 | 126.4205 | 480 | 20 | 25 | 30 | 2 | 3 | 1 | 125 | 480 | 125 | 480 | 125 | 480 | 125 | 480
|  | Doors - Hollow-core | Hollow core sgle doors incl frm plywood facing | Hollow core dble doors incl frm plywood facing | no | 380 | 380 | 380 | 333.75 | 537.5 | 25 | 35 | 40 | 3 | 2 | 3 | 345 | 555 | 325 | 525 | 325 | 525 | 340 | 545
|  | Doors - Solid | Solid core single door incl frame | Solid core double door incl frame | no | 600 | 600 | 600 | 447.5 | 767.5 | 40 | 50 | 60 | 3 | 3 | 4 | 460 | 785 | 440 | 755 | 440 | 755 | 450 | 775
|  | Fire Doors | 1/2 hour single | 2 hour double | no | 1600 | 1857.3627 | 1857.3627 | 1215 | 3105 | 40 | 50 | 60 | 5 | 5 | 4 | 1420 | 3580 | 1420 | 3580 | 1420 | 3580 | 1420 | 3580
|  | Metal Doors | Zintec metal clad single door | Stainless steel clad single door | no | 615 | 779.3937 | 990 | 880 | 1135 | 40 | 50 | 60 | 3 | 3 | 3 | 880 | 1095 | 855 | 1135 | 855 | 450 | 870 | 465
|  | Metal Roller Door | Continuous curtain | Interlocking slat | m2 | 170 | 187.1014 | 187.1014 | 156.25 | 360 | 28 | 35 | 42 | 3 | 2 | 3 | 170 | 375 | 170 | 380 | 175 | 400 | 175 | 425
|  | Paint Finish (per leaf) | Base quality typical door | High quality larger door (860x1980) | no | 65 | 72.7665 | 72.7665 | 61.25 | 85 | 8 | 10 | 12 | 2 | 1 | 3 | 65 | 100 | 65 | 100 | 65 | 100 | 65 | 100
|  | Polyurethane Finish (per leaf) | Base quality typical door | High quality larger door (860x1980) | no | 65 | 70.5262 | 70.5262 | 60 | 81.25 | 8 | 10 | 12 | 2 | 1 | 3 | 60 | 95 | 60 | 95 | 60 | 95 | 60 | 95
|  | Sliding Doors (Cavity) | Cavity slider with hollow core door | Double solid core cavity slider | no | 1300 | 1300 | 1300 | 1152.5 | 2203.75 | 40 | 50 | 60 | 3 | 2 | 3 | 1170 | 2270 | 1135 | 2175 | 1150 | 2185 | 1155 | 2185
|  | Swing Doors - (pair) ( Smoke Stop) | 1/2 hour double | 2 hour double | no | 2325 | 2325 | 2780 | 2655 | 2905 | 40 | 50 | 60 | 5 | 5 | 4 | 2655 | 2875 | 2685 | 2905 | 1660 | 1845 | 1680 | 1870
|  | Timber Glass | 1980 x 760 single safety glass panel | 1980 x 760 two safety glass panel | no | 1210 | 1210 | 1210 | 1190 | 1220 | 40 | 50 | 60 | 3 | 3 | 3 | 1190 | 1220 | 1190 | 1220 | 1190 | 1220 | 1190 | 1220
| Interior Walls | Int Window - Metal | 10mm tough clear glazed screen, al frame | 10mm tough tinted glazed screen, al frame | m2 | 500 | 524.732 | 524.732 | 475 | 540 | 20 | 25 | 35 | 3 | 2 | 3 | 500 | 565 | 500 | 565 | 500 | 565 | 500 | 565
|  | Int Window - Timber | Timber framed glazed screen, 4mm clear | Timber framed glazed, 6mm toughened | m2 | 550 | 560 | 560 | 540 | 585 | 20 | 25 | 35 | 3 | 2 | 3 | 540 | 600 | 540 | 600 | 540 | 600 | 540 | 600
|  | Proprietary | Office partitions incl steel frame & gib | High spec partitions incl steel frame & gib - braced | m2 | 125 | 121.4554 | 162 | 150 | 175.1078 | 20 | 25 | 30 | 4 | 3 | 4 | 150 | 155 | 150 | 155 | 150 | 155 | 155 | 160
| Wall Finishes | Fibrolite | Hardiflex | 9 thick Villaboard | m2 | 55 | 61.5152 | 60 | 52 | 68 | 60 | 75 | 90 | 3 | 2 | 2 | 46 | 66 | 46 | 66 | 46 | 68 | 48 | 68
|  | Gib-board Lining | 10mm Gib | 16mm Gib Fyreline | m2 | 38 | 48.8133 | 51.0955 | 34 | 61.2364 | 40 | 50 | 60 | 3 | 2 | 2 | 36 | 56 | 38 | 58 | 36 | 60 | 36 | 62
|  | Glass | 10mm toughened clear glass in alum. frame | 10mm toughened tinted glass in alum. frame | m2 | 50 | 46.9351 | 46.9351 | 45.1172 | 55 | 40 | 50 | 60 | 4 | 4 | 3 | 500 | 565 | 500 | 565 | 500 | 565 | 500 | 565
|  | Hardboard | 3 thick Hardboard | 6 thick, tempered | m2 | 30 | 35.0209 | 35.0209 | 26 | 45 | 30 | 35 | 45 | 3 | 2 | 2 | 28 | 48 | 28 | 48 | 28 | 50 | 28 | 50
|  | Melteca / Seratone | Seratone | 6mm thick Hardiglaze Premium | m2 | 135 | 167.3137 | 173.0343 | 156 | 184 | 40 | 50 | 60 | 2 | 2 | 2 | 158 | 174 | 156 | 178 | 156 | 184 | 156 | 184
|  | Paint Finish | Acrylic, seal, two coats semi-gloss | Enamel, sealer, undercoat, one coat semi-gloss/gloss | m2 | 18 | 19 | 19 | 17 | 22 | 8 | 10 | 12 | 2 | 1 | 3 | 16 | 18 | 16 | 18 | 16 | 18 | 16 | 18
|  | Particle Board | Kopine Ultralock | Pynefloor Gold | m2 | 50 | 50.5884 | 51.0748 | 48 | 55.5481 | 60 | 75 | 90 | 3 | 2 | 2 | 50 | 54 | 48 | 52 | 50 | 52 | 52 | 54
|  | Plaster Finish | Hardwall plaster, 4mm thick, plain | With narrow widths and angles | m2 | 60 | 56 | 70.2593 | 52.3896 | 105.9725 | 40 | 50 | 60 | 3 | 2 | 3 | 54 | 68 | 52 | 66 | 52 | 66 | 52 | 66
|  | Plywood | 7mm plywood | 21 thick plywood | m2 | 80 | 71.123 | 74.7449 | 55.4401 | 99.2461 | 60 | 75 | 90 | 3 | 1 | 2 | 56 | 98 | 52 | 90 | 52 | 90 | 54 | 96
|  | Tiles - Ceramic | 150 x 150 ceramic | 200 x 100 ceramic | m2 | 155 | 155 | 161.5202 | 154.8613 | 164.7734 | 40 | 50 | 60 | 3 | 1 | 3 | 155 | 165 | 155 | 165 | 155 | 165 | 155 | 165
|  | Timber Lining | Plywood | Slice cut veneer MDF | m2 | 175 | 183.2111 | 166 | 150 | 181.6657 | 60 | 75 | 90 | 3 | 1 | 3 | 58 | 194 | 58 | 190 | 58 | 182 | 58 | 178
|  | Wallpaper Finish | PC $30 a roll | Imported vinyl fabric pc $17/m2 | m2 | 30 | 30 | 30 | 22 | 46 | 8 | 10 | 12 | 2 | 1 | 3 | 22 | 46 | 22 | 46 | 22 | 46 | 22 | 46
Services | Electrical | Cabling / Internal Wiring | Light | Heavy | m2 | 35 | 48.3333 | 59.2083 | 18.75 | 96 | 32 | 40 | 48 | 5 | 2 | 1 | 25 | 120 | 25 | 120 | 25 | 120 | 25 | 120
|  | Display Lights | 150W spot light, fixed to light track | 12v spot light with inbuilt transformer, fixed to track | no | 280 | 336.7173 | 414.4213 | 215.3846 | 424.6154 | 12 | 15 | 18 | 4 | 3 | 3 | 240 | 480 | 240 | 480 | 240 | 480 | 240 | 480
|  | Emergency Lights | Simple small light | Larger light | no | 445 | 547.801 | 638 | 580 | 695 | 20 | 25 | 30 | 5 | 5 | 3 | 580 | 695 | 580 | 695 | 580 | 695 | 580 | 695
|  | Exit Signs(Illuminated) | Thorn ECON110S | Stanilite LSNCS122 Legend Maint Monitored | no | 570 | 695 | 847.123 | 770 | 925 | 12 | 15 | 18 | 4 | 2 | 3 | 770 | 925 | 770 | 925 | 770 | 925 | 770 | 925
|  | Flood Lights | Thorn FF150B | 2000 watt metal halide discharge | no | 250 | 319.6259 | 391.8534 | 141.5385 | 5770.0797 | 12 | 15 | 18 | 3 | 4 | 4 | 160 | 6515 | 160 | 6515 | 160 | 6515 | 160 | 6515
|  | Fluorescent Lights | Fluorescent, batten, 2x36w | Fluorescent, recessed, grid ceiling, 3x36w | no | 250 | 329.7991 | 402.4481 | 219.5122 | 512.8421 | 20 | 25 | 30 | 3 | 3 | 3 | 250 | 580 | 250 | 580 | 250 | 580 | 250 | 580
|  | Incandescent Lights | Batten lampholder | Pendant, 3 light type | no | 110 | 123.75 | 123.75 | 50 | 675 | 12 | 15 | 18 | 3 | 3 | 3 | 50 | 675 | 50 | 675 | 50 | 675 | 50 | 675
|  | Light Switches & Powerpoints | Light | Heavy | no | 275 | 275 | 330.1274 | 150.8621 | 1020.8955 | 24 | 30 | 36 | 3 | 2 | 3 | 175 | 1200 | 175 | 1200 | 175 | 1200 | 175 | 1200
|  | Local DBS | 9 pole single phase | 48 way 144 pole three phase with controls | no | 2500 | 3005.4012 | 3498.4512 | 573.6449 | 26833.8462 | 32 | 40 | 48 | 4 | 3 | 1 | 620 | 30780 | 620 | 30780 | 620 | 30780 | 620 | 30780
|  | Local Security Lighting | Batten lampholder | 2000 watt metal halide discharge | no | 500 | 575 | 638.5895 | 50 | 5770.0797 | 12 | 15 | 18 | 5 | 4 | 3 | 50 | 6515 | 50 | 6515 | 50 | 6515 | 50 | 6515
|  | Main Fusebox | 9 pole single phase | 12 way 36 pole three phase | no | 1500 | 700 | 762.6316 | 483.3684 | 1950 | 32 | 40 | 48 | 5 | 4 | 2 | 560 | 985 | 560 | 985 | 560 | 985 | 560 | 985
|  | Main Switch Board | Small | Large public building | no | 5000 | 6500 | 7657.8808 | 2781.5872 | 222246.8944 | 32 | 40 | 48 | 5 | 4 | 2 | 3205 | 256500 | 3205 | 256500 | 3205 | 256500 | 3205 | 256500
|  | Meter Boxes | Hicks HP1 | Hicks HP7 | no | 600 | 893.4243 | 900 | 650 | 1150 | 32 | 40 | 48 | 5 | 4 | 2 | 650 | 1150 | 650 | 1150 | 650 | 1150 | 650 | 1150
|  | Pole Top Lights (External) | 80 watt mercury in 550 dia opal sphere | Bega 150 watt sodium on 7.6 m. pole | no | 2500 | 3292.4364 | 3805.6418 | 1302.6446 | 4925.9494 | 12 | 15 | 18 | 4 | 3 | 2 | 1480 | 5590 | 1480 | 5590 | 1480 | 5590 | 1480 | 5590
| Fire Services | EWIS system | System complete, for minor installation | System complete, major installation | no | 30000 | 20000 | 33862.6667 | 15525 | 42190 | 15 | 18 | 20 | 3 | 3 | 2 | 15525 | 42190 | 15525 | 42190 | 15525 | 42190 | 15525 | 42190
|  | Ext. Alarm Panel / Fire Sys. | Minor project | Major project | no | 3500 | 3888.5691 | 3888.5691 | 3040 | 40500 | 30 | 40 | 50 | 5 | 5 | 2 | 3715 | 40500 | 3715 | 40500 | 3715 | 40500 | 3715 | 40500
|  | Fire - Heat detectors | Typical product | Typical product | no | 120 | 130.1338 | 132 | 115 | 135 | 28 | 35 | 42 | 5 | 5 | 3 | 130 | 135 | 130 | 135 | 130 | 135 | 130 | 135
|  | Fire Alarm System | Refer to External Indicator board item above | Refer to External Indicator board item above | no | 5000 | 5000 | 5000 | 2000 | 25000 | 12 | 15 | 18 | 5 | 5 | 3 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
|  | Fire Extinguishers | 2.25 kg dry powder | 5 kg CO2 | no | 350 | 350 | 350 | 160 | 500 | 16 | 20 | 24 | 5 | 5 | 3 | 160 | 500 | 160 | 500 | 160 | 500 | 160 | 500
|  | Fire Hose reels | Standard 20m x 13 dia | Surface cabinet 20m x 19 dia | no | 615 | 710.5184 | 710.5184 | 395 | 945 | 12 | 15 | 18 | 5 | 5 | 3 | 455 | 1095 | 455 | 1095 | 455 | 1095 | 455 | 1095
|  | Fire Sprinklers | Standard head exposed | Standard head flush mounted | no | 295 | 343.7197 | 335 | 320 | 350 | 25 | 30 | 40 | 5 | 5 | 3 | 320 | 350 | 320 | 350 | 320 | 350 | 320 | 350
|  | Pipework | Fire_Pipework_25 dia, screw fittings | Fire_Pipework_150 dia, grooved end joints & fittings | m | 80 | 54 | 54 | 50 | 300 | 7 | 20 | 30 | 4 | 3 | 2 | 35 | 195 | 35 | 195 | 35 | 195 | 35 | 195
|  | Smoke Detectors | Combustion type | Photo optic type | no | 230 | 248.8889 | 270 | 255 | 285 | 8 | 10 | 12 | 5 | 5 | 4 | 255 | 285 | 255 | 285 | 255 | 285 | 255 | 285
|  | Valves - fire system | Hydrant point, 80mm, single storey building | Hydrant point, 80mm, 2-10 storey building | no | 1000 | 2000 | 2000 | 1000 | 3500 | 8 | 12 | 25 | 4 | 3 | 2 | 1890 | 2445 | 1890 | 2445 | 1890 | 2445 | 1890 | 2445
|  | Ventilating Fans | 3.5m3/s roof extract | 23 m3/s roof extract | no | 8600 | 8600 | 10114.6191 | 3755 | 18460 | 20 | 25 | 30 | 4 | 4 | 2 | 3755 | 18460 | 3755 | 18460 | 3755 | 18460 | 3755 | 18460
| Lifts / Hoist | Car Interior & Call Buttons | Basic spec, small car | High spec, large car | no | 12000 | 16200 | 16200 | 5000 | 20000 | 7 | 10 | 15 | 4 | 3 | 3 | 6750 | 27000 | 6750 | 27000 | 6750 | 27000 | 6750 | 27000
|  | Cleaner Cradle - BMU | Small movable | Large permanent ftted to top of building | no | 35000 | 35000 | 35000 | 16200 | 270000 | 20 | 25 | 30 | 5 | 4 | 2 | 16200 | 270000 | 16200 | 270000 | 16200 | 270000 | 16200 | 270000
|  | Controller | Electronic variable frequency, small car | Electronic variable frequency, large car | no | 20000 | 100000 | 135000 | 67500 | 202500 | 7 | 10 | 15 | 3 | 3 | 3 | 67500 | 202500 | 67500 | 202500 | 67500 | 202500 | 67500 | 202500
|  | Door sets | Door operator and landing sets, low spec | Door operator and landing sets, high spec | no | 5000 | 14000 | 14000 | 13500 | 14850 | 10 | 15 | 20 | 3 | 3 | 3 | 13500 | 14850 | 13500 | 14850 | 13500 | 14850 | 13500 | 14850
|  | Escalators | 600 wide standard 3 m. rise | 1000 wide superior 5 m. rise | no | 210000 | 210000 | 210000 | 189000 | 256500 | 20 | 25 | 30 | 4 | 4 | 4 | 189000 | 256500 | 189000 | 256500 | 189000 | 256500 | 189000 | 256500
|  | Goods and Service Lift | 2 floors 450 kg | 10 floors 2000 kg | no | 165000 | 165000 | 165000 | 54000 | 573750 | 35 | 40 | 50 | 2 | 3 | 2 | 54000 | 573750 | 54000 | 573750 | 54000 | 573750 | 54000 | 573750
|  | Motor | Motor, up to 10Kw | Motor, over 10Kw | no | 20000 | 45000 | 80000 | 27000 | 135000 | 20 | 50 | 60 | 3 | 3 | 2 | 27000 | 135000 | 27000 | 135000 | 27000 | 135000 | 27000 | 135000
|  | Passenger Lift - Hydraulic | 2 floors 8 passenger 0.4 m/s | 5 floors 30 passenger 0.5 m/s | no | 155000 | 155000 | 155000 | 108000 | 195750 | 20 | 25 | 30 | 5 | 4 | 3 | 108000 | 195750 | 108000 | 195750 | 108000 | 195750 | 108000 | 195750
|  | Passenger Lift - Traction | 4 floors 13 passenger 1.0 m/s hydraulic | 20 floors 17 passenger 6.0 m/s variable speed | no | 550000 | 550000 | 550000 | 270000 | 783000 | 35 | 40 | 50 | 5 | 4 | 3 | 270000 | 783000 | 270000 | 783000 | 270000 | 783000 | 270000 | 783000
|  | Pulley hoists | 1 ton manual | 5 ton electric with trolley | no | 5000 | 5000 | 5000 | 540 | 20250 | 20 | 25 | 30 | 4 | 3 | 2 | 540 | 20250 | 540 | 20250 | 540 | 20250 | 540 | 20250
|  | Ropes | Ropes, small car | Ropes, large car | no | 15000 | 1687.5 | 2025 | 1350 | 2700 | 5 | 7 | 10 | 4 | 4 | 2 | 1350 | 2700 | 1350 | 2700 | 1350 | 2700 | 1350 | 2700
|  | Stage lift | Simple low height | Large, enclosed and high | no | 200000 | 250000 | 250000 | 35000 | 450000 | 35 | 40 | 50 | 4 | 4 | 2 | 162000 | 405000 | 162000 | 405000 | 162000 | 405000 | 162000 | 405000
|  | Walkways (moving) | 1000 wide 30 m. long | 1000 wide inclined 10 deg. 30 m long | no | 425000 | 425000 | 425000 | 398250 | 479250 | 20 | 25 | 30 | 3 | 4 | 4 | 398250 | 479250 | 398250 | 479250 | 398250 | 479250 | 398250 | 479250
|  | Winch gear |  |  | no | 30000 | 30000 | 30000 | 20000 | 150000 | 20 | 50 | 60 | 3 | 3 | 2 | 20000 | 150000 | 20000 | 150000 | 20000 | 150000 | 20000 | 150000
| Mechanical | Air Conditioner | 2.5 kW window/wall mounted | 6.5 kW external wall | no | 3500 | 3500 | 3953.3413 | 1755 | 7020 | 9.6 | 12 | 16 | 4 | 4 | 3 | 1755 | 7020 | 1755 | 7020 | 1755 | 7020 | 1755 | 7020
|  | Air Handler Units | Split system A/C, concealed, 472 l/s, 9kW | Split system A/C, concealed, 755 l/s, 16kW | no | 8500 | 8500 | 9656.3288 | 8910 | 12555 | 18 | 20 | 25 | 4 | 4 | 1 | 8910 | 12555 | 8910 | 12555 | 8910 | 12555 | 8910 | 12555
|  | Axial Ventillation Fans | 315mm dia, 500l/sec @40Pa | 1000mm dia, 10,000l/sec @400Pa | no | 7000 | 3500 | 3963.751 | 226.3889 | 22661.1227 | 5 | 20 | 30 | 3 | 3 | 1 | 2445 | 10900 | 2445 | 10900 | 2445 | 10900 | 2445 | 10900
|  | Boilers | 100 kW On/Off | 1500 kW Modulating | no | 25000 | 25000 | 28848.8775 | 15120 | 83295 | 16 | 20 | 24 | 5 | 4 | 1 | 15120 | 83295 | 15120 | 83295 | 15120 | 83295 | 15120 | 83295
|  | Building Management System | Energy Management system, control unit 1 to 8 items of plant | Energy Management system, control unit for 21 to 40 items of plant | no | 70000 | 8000 | 15000 | 6750 | 28020 | 7 | 10 | 15 | 5 | 4 | 3 | 6750 | 28020 | 6750 | 28020 | 6750 | 28020 | 6750 | 28020
|  | Centrifugal Ventilation Fans | Single Width Single Inlet, 2300/500 | Double WidthDouble Inlet, 20000/1500 | no | 5000 | 23850 | 26743.903 | 1112.9032 | 33893.1624 | 5 | 15 | 20 | 3 | 3 | 2 | 9315 | 39655 | 9315 | 39655 | 9315 | 39655 | 9315 | 39655
|  | Chillers - Centrifigal | 500 kW Centrifugal | 1400 kW Centrifugal | no | 150000 | 200000 | 371250 | 270000 | 472500 | 14 | 18 | 22 | 3 | 3 | 3 | 270000 | 472500 | 270000 | 472500 | 270000 | 472500 | 270000 | 472500
|  | Chillers - Recpricating | 120 kW reciprocating | 700kW reciprocating | no | 80000 | 130000 | 147773.2323 | 11345.4545 | 193611.1111 | 14 | 18 | 22 | 3 | 3 | 3 | 84240 | 276750 | 84240 | 276750 | 84240 | 276750 | 84240 | 276750
|  | Chillers - Screw | 115KW | 720KW | no | 120000 | 150000 | 150082.4373 | 24758.6619 | 303225.8065 | 14 | 18 | 22 | 3 | 3 | 3 | 103615 | 317250 | 103615 | 317250 | 103615 | 317250 | 103615 | 317250
|  | Cooling Tower | 40 ton Refrig | 160 ton Refrig | no | 24000 | 24000 | 27226.1658 | 22210 | 31390 | 14.4 | 18 | 21.6 | 4 | 4 | 2 | 22210 | 31390 | 22210 | 31390 | 22210 | 31390 | 22210 | 31390
|  | Ductwork | Plain straight duct | 50 acoustic in fittings | m2 | 80 | 80 | 87.4026 | 75 | 245 | 20 | 25 | 30 | 3 | 2 | 1 | 75 | 245 | 75 | 245 | 75 | 245 | 75 | 245
|  | Fan Coil Units | Ceiling mounted FCU, filter, heater, cooling system | Ceiling mounted FCU, filter, heater, cooling system | no | 2000 | 2000 | 2240.8459 | 1855 | 2800 | 14.4 | 18 | 22 | 3 | 4 | 2 | 1855 | 2800 | 1855 | 2800 | 1855 | 2800 | 1855 | 2800
|  | Fireplaces | Residential | Commercial setting | no | 5000 | 5000 | 5000 | 3580 | 7765 | 60 | 75 | 90 | 3 | 2 | 3 | 3580 | 7765 | 3580 | 7765 | 3580 | 7765 | 3580 | 7765
|  | Flues | 150 dia light duty insulated | 450 dia boiler flue insulated | m | 400 | 400 | 470.0767 | 400 | 1080 | 40 | 50 | 60 | 3 | 2 | 3 | 400 | 1080 | 400 | 1080 | 400 | 1080 | 400 | 1080
|  | Header Tank | 2,000 litre | 7,000 litre | no | 5000 | 3500 | 3500 | 1000 | 10000 | 15 | 20 | 40 | 3 | 2 | 1 | 1720 | 4255 | 1720 | 4255 | 1720 | 4255 | 1720 | 4255
|  | Heat Exchanger, chilled water | Chilled water type, plate-style heat exchanger, small, 25kW | Chilled water type, shell & tube heat exchanger, large, 200kW | no | 20000 | 20000 | 20000 | 7090 | 32400 | 20 | 25 | 30 | 3 | 2 | 2 | 7090 | 32400 | 7090 | 32400 | 7090 | 32400 | 7090 | 32400
|  | Heat Exchanger, heating | Heating type, plate-style heat exchanger, small, 25kW | Heating type, shell & tube heat exchanger, large, 200kW | no | 10000 | 10000 | 10000 | 3715 | 16200 | 20 | 25 | 30 | 3 | 2 | 2 | 3715 | 16200 | 3715 | 16200 | 3715 | 16200 | 3715 | 16200
|  | Piping | 20mm black mild steel, incl fittings | 100mm black mild steel, 1 fitting per 10m | m | 90 | 90 | 100.2434 | 36.25 | 167.2648 | 20 | 25 | 30 | 2 | 1 | 1 | 35 | 115 | 40 | 185 | 35 | 185 | 35 | 185
|  | Radiators (oil) | 1 kW water-fed radiator | 3 kW water-fed radiator | no | 800 | 800 | 909.8412 | 890 | 1620 | 24 | 30 | 36 | 4 | 2 | 3 | 890 | 1620 | 890 | 1620 | 890 | 1620 | 890 | 1620
|  | Space Heaters | Infra red strip heater, 1100W | Panel heater, 2000W wall mounted | no | 600 | 826.3283 | 971.4023 | 398.1579 | 1357.0881 | 20 | 25 | 30 | 3 | 4 | 3 | 445 | 1540 | 445 | 1540 | 445 | 1540 | 445 | 1540
|  | Split Air Conditioning Units | 5.2 kW non-ducted, wall mounted | 13.6 kW under ceiling | no | 5500 | 5500 | 6239.7341 | 5290.0747 | 14380 | 9.6 | 12 | 16 | 4 | 4 | 3 | 5065 | 14380 | 5365 | 14380 | 5365 | 14380 | 5365 | 14380
|  | Underflr/wall &/or Ceiling Heat. | Electric | Water fed | m2 | 115 | 132.1062 | 156.9733 | 84 | 176.4706 | 30 | 35 | 50 | 2 | 3 | 1 | 90 | 200 | 90 | 200 | 90 | 200 | 90 | 200
|  | Valves - HVAC | Bronze Gate Valve, 25mm dia | Cast Iron Globe Valve, 150mm dia | no | 1000 | 478.6667 | 505.2431 | 85 | 4320 | 8 | 12 | 25 | 3 | 2 | 1 | 85 | 4320 | 85 | 4320 | 85 | 4320 | 85 | 4320
|  | Water Pump | 2 litre/sec @ 2m head | 30 litre/sec @ 18m head | no | 1800 | 1800 | 2039.8822 | 980 | 7425 | 5.6 | 7 | 9 | 4 | 2 | 1 | 980 | 7425 | 980 | 7425 | 980 | 7425 | 980 | 7425
| Sanitary Plumbing | Bath | acrylic1525 long,2 taps, minor carpentry work | acrylic 1800 long,2 taps, minor carpentry work | no | 900 | 989.0644 | 914.9149 | 710.8593 | 1290.4631 | 40 | 50 | 60 | 2 | 2 | 2 | 790 | 1370 | 765 | 1350 | 765 | 1350 | 765 | 1350
|  | Handbasin | wall mount&brackets,acrylic, 2 taps,connex | wall mount&brackets,vit china, 2 taps,connex | no | 750 | 695.1921 | 857 | 790 | 940 | 28 | 35 | 42 | 4 | 5 | 3 | 815 | 940 | 790 | 910 | 790 | 910 | 790 | 910
|  | Laundry Tub | Stainless Steel ,brackets,2 taps,connex | Twin steel,brackets,2 taps,timber cabinet | no | 850 | 879.6545 | 914.8059 | 815.127 | 1370.9851 | 40 | 50 | 60 | 3 | 3 | 2 | 875 | 1415 | 855 | 1395 | 855 | 1395 | 855 | 1395
|  | Shower Unit (acrylic 3 sided) | base&waste, line 3 sides,curtain,mixer & rose | tiled foor & walls & glass enclosure | no | 2200 | 2500 | 4363 | 2470 | 6470 | 20 | 25 | 30 | 5 | 5 | 3 | 2515 | 6485 | 2455 | 6465 | 2455 | 6465 | 2455 | 6465
|  | Tap | Generic basin tap or Faucet | Methven Classical Nilo NL92 basin faucet | no | 140 | 151.6956 | 176.3406 | 130.5161 | 539.2158 | 16 | 20 | 24 | 4 | 3 | 3 | 180 | 585 | 175 | 580 | 175 | 580 | 175 | 580
|  | Toilet - China Bowl /Cistern | Vit. China,plastic seat&cistrn.cistrn tap | Caroma Walvit wc suite&water wafer inwall cist, cistern tap | no | 136 | 136 | 156.0765 | 145.9662 | 165.9701 | 30 | 35 | 45 | 4 | 4 | 3 | 150 | 170 | 145 | 165 | 145 | 165 | 145 | 165
|  | Toilet - China Urinal | 5 litre steel cistern & china wall hung | 28 litre ss cistern.Vitrous china wall hung urinal, trap | no | 3007 | 3007 | 3006.4086 | 1883.4577 | 3912.9394 | 30 | 35 | 45 | 4 | 4 | 4 | 1910 | 3950 | 1875 | 3900 | 1875 | 3900 | 1875 | 3900
|  | Toilet - S/S Bowl /Cistern | Floor mounted | Mc Donald industries back inlet stainless steel | no | 2878 | 2878 | 5483.656 | 3706.8172 | 7571.4327 | 30 | 35 | 45 | 4 | 4 | 3 | 3715 | 7560 | 3715 | 7560 | 3715 | 7560 | 3715 | 7560
|  | Toilet - S/S Urinal | 5 litre ss cistern. 900 long SS slab urinal. Push button | 28 litre ss cistern.ss slab urinal, trap, tread, 1800mm, water saver IR sensor | no | 6458 | 6458 | 6387.7862 | 4891.2762 | 7913 | 30 | 35 | 45 | 4 | 4 | 3 | 4900 | 7925 | 4890 | 7910 | 4890 | 7910 | 4890 | 7910
|  | Vanity (incl Basin) | 750 long completely melamine | 1500 long timber veneer | no | 4500 | 4500 | 1740 | 1115 | 2365 | 20 | 25 | 30 | 4 | 4 | 3 | 1115 | 2365 | 1115 | 2365 | 1115 | 2365 | 1115 | 2365
| Special Services | Barrier arms | Typical arms | Additional features | no | 4400 | 4400 | 4400 | 2000 | 5000 | 16 | 20 | 24 | 3 | 3 | 3 | 4320 | 0 | 4320 | 0 | 4320 | 0 | 4320 | 0
|  | Card Reader | Proximity reader | Card reader | no | 3500 | 3500 | 3899.859 | 810 | 6885.6911 | 16 | 20 | 24 | 3 | 3 | 2 | 810 | 8710 | 810 | 8710 | 810 | 8710 | 810 | 8710
|  | CCTV Camera / Monitor | Fixed lens internal | Zoom lens low light external | no | 1000 | 1419.2847 | 1675 | 1390 | 1960 | 5.6 | 7 | 9 | 4 | 3 | 4 | 1390 | 1960 | 1390 | 1960 | 1390 | 1960 | 1390 | 1960
|  | Elect. Security Sys. - Domestic | Basic | Additional detection | no | 1500 | 1400 | 1718.1542 | 954.2132 | 1939.0704 | 12 | 15 | 18 | 5 | 4 | 2 | 1205 | 2450 | 1205 | 2450 | 1205 | 2450 | 1205 | 2450
|  | Generators (Standby) | 7 kVA | 100 kVA | no | 20000 | 27528.0294 | 34103.4779 | 15552.2807 | 236249.7088 | 16 | 20 | 24 | 5 | 5 | 1 | 31660 | 133450 | 31660 | 133450 | 31660 | 133450 | 31660 | 133450
|  | Parking Control | Ticket dispenser, basic | Ticket dispenser, magnetic stripe | no | 10000 | 13443.75 | 13443.75 | 5000 | 60000 | 5 | 10 | 15 | 3 | 3 | 2 | 11475 | 23625 | 11475 | 23625 | 11475 | 23625 | 11475 | 23625
|  | Surveillance and Security System | Camera, dome, 4 camera switcher, 4 camera recorder, monitor | Camera, external housing, 16 camera switcher, 16 camera recorder, monitor | no | 35000 | 12000 | 12550.8065 | 5246.8393 | 208486.6469 | 7 | 10 | 15 | 4 | 4 | 2 | 8715 | 17565 | 8715 | 17565 | 8715 | 17565 | 8715 | 17565

## Survey Form
Property Name | [5 empty] | Surveyor |  |  |  |  | Survey Date
Component Group | Component Type | Component | Condition Grade (% split) & Assessed Remaining Life |  |  |  |  | qty | Unit | Rate | Comments | Base Life
| Component Type | Asset | 1 | 2 | 3 | 4 | 5
External Fabric | External Walls | Brick Cladding | [5 empty] | 5000 | m2 | 163
External Fabric | Roof | Metal Roofing | [5 empty] | 600 | m2 | 56
External Fabric | Windows & Doors | Aluminium Windows | [5 empty] | 200 | m2 | 486
External Fabric | Windows & Doors | Timber Entrance Door | [5 empty] | 30 | no | 900
FPE-Electrical Services | Lighting | Exit Signs(Illuminated) | [5 empty] | 30 | no | 847
FPE-Electrical Services | Lighting | Flood Lights | [5 empty] | 15 | no | 391
FPE-Electrical Services | Lighting | Fluorescent Lights | [5 empty] | 889 | no | 402
FPE-Fire Services | Fire Extinguishers | Fire Extinguishers | [5 empty] | 15 | no | 350
FPE-Water Services | Sanitary Plumbing | Handbasin | [5 empty] | 10 | no | 857
FPE-Water Services | Sanitary Plumbing | Tap | [5 empty] | 10 | no | 176
FPE-Water Services | Sanitary Plumbing | Toilet - China Bowl /Cistern | [5 empty] | 10 | no | 156
Interior Finishes | Ceiling Finishes | Gib-board Lining | [5 empty] | 2000 | m2 | 51
Interior Finishes | Ceiling Finishes | Paint Finish | [5 empty] | 4000 | m2 | 19
Interior Finishes | Ceiling Finishes | Plaster Finish | [5 empty] | 2000 | m2 | 70
Interior Finishes | Ceiling Finishes | Suspended Panel (Incl Frame) | [5 empty] | 1100 | m2 | 79
Interior Finishes | Fixtures & Fittings | Joinery Fttgs - Built-In | [5 empty] | 30 | m | 1049
Interior Finishes | Fixtures & Fittings | Mirror | [5 empty] | 10 | ea | 260
Interior Finishes | Floor Finishes | Carpet | [5 empty] | 2000 | m2 | 95
Interior Finishes | Floor Finishes | Ceramic Tiles | [5 empty] | 1000 | m2 | 152
Interior Finishes | Floor Finishes | Vinyl | [5 empty] | 1000 | m2 | 47
Interior Finishes | Interior Doors | Door Closer | [5 empty] | 50 | no | 300
Interior Finishes | Interior Doors | Doors - Hollow-Core | [5 empty] | 30 | no | 380
Interior Finishes | Interior Doors | Doors - Solid | [5 empty] | 20 | no | 600

## Condition Grading
| 1 | 2 | 3 | 4 | 5
| Very Good Condition | Good Condition | Moderate Condition | Poor Condition | Very Poor Condition
Estimated Proportion of life consumed | Up to 45% | Between 45% to 90% |  |  | Up to 90%
Structure | Sound structure. | Functionally sound structure. | Adequate structure, some evidence of foundation movement, minor cracking. | Structure functioning but with problems due foundation movement, Some significant cracking. | Structure has serious problems and concern is held for the integrity of the structure.
External | Fabric constructed with sound materials, true to line and level. No evidence of deterioration or discolouration. | Showing minor wear and tear and minor deterioration of surfaces. | Appearance affected by minor cracking, staining, or minor leakage. Indications of breaches of weatherproofing. Minor damage to coatings. | Fabric damaged, weakened or displaced. Appearance affected by cracking, staining, overflows, or breakages. Breaches of weatherproofing evident. Coatings in need of heavy maintenance or renewal. | Fabric is badly damaged or weakened. Appearance affected by cracking, staining, overflows, leakage, or wilful damage. Breaches of waterproofing. Coatings badly damaged or non-existent.
Internal |  |  | Appearance affected by minor cracking, staining, or minor leakage, some dampness or mildew. Minor damage to wall/ceiling finishes | Fabric damaged, weakened or displaced. Appearance affected by cracking, staining, dampness, leakage, or breakages. Breaches of waterproofing evident. Finishes of poor quality and in need of replacement. | Fabric badly damaged or weakened. Appearance affected by cracking, staining, leakage, or wilful damage. Breaches of waterproofing. Finishes badly damaged, marked and in need of replacement.
Services | All components operable and well maintained. | All components operable | Occasional outages, breakdowns or blockages. Increased maintenance required | Failures of plumbing electrical and mechanical components common place. | Plumbing electrical and mechanical components are unsafe or inoperable
Fittings | Well secured and operational, sound of function and appearance | Operational and functional, minor wear and tear | Generally operational. Minor breakage | Fittings of poor quality and appearance, often inoperable and damaged. | Most are inoperable or damaged
Maintenance | Well maintained and clean | Increased maintenance inspection required | Regular and programmed maintenance inspections essential | Frequent maintenance inspections essential. Short term element replacement rehabilitation. | Minimum life expectancy, requiring urgent rehabilitation or replacement
Customers | No customer concerns | Deterioration causes minimal influence on occupational uses. Occasional customer concerns | Some deterioration beginning to be reflected in minor restrictions on operational uses. Customer concerns. | Regular customer complaints. | Generally not suitable for use by customers
Important Notes
Immediate maintenance | Small items of immediate maintenance which if repaired in the short term will restore the element to a higher condition grade. In such an instance the surveyor will both grade the element at the higher condition grade and report the immediate maintenance required.
Grade 1 | Many surveyors are reluctant to assess an element as grade 1, opting for the “conservative” assessment of grade 2. This is a poor practice as it artificially brings forward predictions of future expenditure on that element. As a guide an element will generally remain in grade 1 for 35 – 50% of its overall life.
Services | Services relate to all plumbing electrical and mechanical components

## Renewals Key
Prepared for www.nams.au.com National Asset Management Strategy Australia by SPM Consultants Ltd www.spmassets.com
Key to Errors - SPM's Condition Based Renewals Analysis
10 | = | The sum of condition percentage in columns C1 to C5 doesn't sum to 100
20 | = | The percentage value in column Cn doesn't have a corresponding assessed remaining life in column Rn
30 | = | The assessed remaining life is greater than that shown in the column to the left (Rn+1 is greater than Rn)
40 | = | The assessed remaining life is greater than the base life
Spreadsheet contains formulae for 1000 rows.

## Assets
| Property Categorisations |  |  | Component descriptions (BCGs) |  |  | Component data | [17 empty] | 1st Year of Planning | [99 empty] | No
Category 1 | Category 2 | Category 3 | property name | Component Group | Component Type | Component | survey | base life | GRC | c1 | c2 | c3 | c4 | c5 | r1 | r2 | r3 | r4 | r5 | y1 | y2 | y3 | y4 | y5 | 2011 | 2012 | 2013 | 2014 | 2015 | 2016 | 2017 | 2018 | 2019 | 2020 | 2021 | 2022 | 2023 | 2024 | 2025 | 2026 | 2027 | 2028 | 2029 | 2030 | 2031 | 2032 | 2033 | 2034 | 2035 | 2036 | 2037 | 2038 | 2039 | 2040 | 2041 | 2042 | 2043 | 2044 | 2045 | 2046 | 2047 | 2048 | 2049 | 2050 | 2051 | 2052 | 2053 | 2054 | 2055 | 2056 | 2057 | 2058 | 2059 | 2060 | 2061 | 2062 | 2063 | 2064 | 2065 | 2066 | 2067 | 2068 | 2069 | 2070 | 2071 | 2072 | 2073 | 2074 | 2075 | 2076 | 2077 | 2078 | 2079 | 2080 | 2081 | 2082 | 2083 | 2084 | 2085 | 2086 | 2087 | 2088 | 2089 | 2090 | 2091 | 2092 | 2093 | 2094 | 2095 | 2096 | 2097 | 2098 | 2099 | 2100 | 2101 | 2102 | 2103 | 2104 | 2105 | 2106 | 2107 | 2108 | 2109 | 2110
Council | Suburb | Location | Building 1 | External Fabric | External Walls | Brick Cladding | 2011 | 75 | 815000 | 0 | 0 | 0 | 0 | 100 |  |  |  |  | 1 | 0 | 0 | 0 | 0 | 1 | 0 | 815000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 815000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | External Fabric | Roof | Metal Roofing | 2011 | 25 | 33600 | 0 | 0 | 100 | 0 | 0 |  |  | 7 |  |  | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 33600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | External Fabric | Windows & Doors | Aluminium Windows | 2011 | 50 | 97200 | 100 | 0 | 0 | 0 | 0 | 15 |  |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 97200 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | External Fabric | Windows & Doors | Timber Entrance Door | 2011 | 50 | 27000 | 100 | 0 | 0 | 0 | 0 | 20 |  |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 27000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Electrical Services | Lighting | Exit Signs(Illuminated) | 2011 | 15 | 25410 | 0 | 0 | 100 | 0 | 0 |  |  | 6 |  |  | 0 | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 25410 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Electrical Services | Lighting | Flood Lights | 2011 | 15 | 5865 | 0 | 0 | 0 | 100 | 0 |  |  |  | 3 |  | 0 | 0 | 0 | 3 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5865 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Electrical Services | Lighting | Fluorescent Lights | 2011 | 25 | 357378 | 0 | 0 | 100 | 0 | 0 |  |  | 8 |  |  | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 357378 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Fire Services | Fire Extinguishers | Fire Extinguishers | 2011 | 20 | 5250 | 100 | 0 | 0 | 0 | 0 | 10 |  |  |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 5250 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Water Services | Sanitary Plumbing | Handbasin | 2011 | 35 | 8570 | 100 | 0 | 0 | 0 | 0 | 15 |  |  |  |  | 35 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 8570 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Water Services | Sanitary Plumbing | Tap | 2011 | 20 | 1760 | 100 | 0 | 0 | 0 | 0 | 15 |  |  |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1760 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | FPE-Water Services | Sanitary Plumbing | Toilet - China Bowl /Cistern | 2011 | 35 | 1560 | 0 | 100 | 0 | 0 | 0 |  | 20 |  |  |  | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 1560 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Ceiling Finishes | Gib-board Lining | 2011 | 50 | 102000 | 100 | 0 | 0 | 0 | 0 | 7 |  |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 102000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Ceiling Finishes | Paint Finish | 2011 | 10 | 76000 | 0 | 100 | 0 | 0 | 0 |  | 25 |  |  |  | 0 | 6 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 76000 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Ceiling Finishes | Plaster Finish | 2011 | 50 | 140000 | 0 | 100 | 0 | 0 | 0 | 20 |  |  |  |  | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 140000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Ceiling Finishes | Suspended Panel (Incl Frame) | 2011 | 50 | 86900 | 100 | 0 | 0 | 0 | 0 | 8 |  |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 86900 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Fixtures & Fittings | Joinery Fttgs - Built-In | 2011 | 40 | 31470 | 100 | 0 | 0 | 0 | 0 | 20 |  |  |  |  | 40 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 31470 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Fixtures & Fittings | Mirror | 2011 | 20 | 2600 | 100 | 0 | 0 | 0 | 0 | 20 |  |  |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 2600 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Floor Finishes | Carpet | 2011 | 15 | 190000 | 50 | 50 | 0 | 0 | 0 | 15 | 12 |  |  |  | 15 | 8 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 95000 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Floor Finishes | Ceramic Tiles | 2011 | 50 | 152000 | 0 | 100 | 0 | 0 | 0 |  | 12 |  |  |  | 0 | 28 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 152000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Floor Finishes | Vinyl | 2011 | 20 | 47000 | 100 | 0 | 0 | 0 | 0 | 10 |  |  |  |  | 20 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 47000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Interior Doors | Door Closer | 2011 | 25 | 15000 | 0 | 0 | 100 | 0 | 0 |  |  | 5 |  |  | 0 | 0 | 9 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 15000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Interior Doors | Doors - Hollow-Core | 2011 | 35 | 11400 | 0 | 100 | 0 | 0 | 0 |  | 25 |  |  |  | 0 | 19 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 11400 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
Council | Suburb | Location | Building 1 | Interior Finishes | Interior Doors | Doors - Solid | 2011 | 50 | 12000 | 100 | 0 | 0 | 0 | 0 | 15 |  |  |  |  | 50 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 12000 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
[20 empty] | 0 | 0 | 0 | 0 | 0
Note on K2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on L2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on M2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on N2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on O2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on P2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on Q2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on R2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on S2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors
Note on T2: Cells showing white numbers on coloured backgrounds indicate errors. Please click on the Key tab at bottom left for explanations of the errors

## Importance
| 26% | 8% | 20% | 20% | 6% | 16% | 4% | 100%
| 130 | 40 | 100 | 100 | 30 | 80 | 20 | 500
Site Name | Site Importance | [6 empty] | Site Importance Factor (SIF)
Site Name | Impact of Failure | Location | Loss of Service | Environmental | Size (WW) / No (water) | Cost of Failure | Site Function
Building 1 | 5 | 2 | 4 | 5 | 5 | 4 | 3 | 4.32 | Site Importance
Building 2 | [8 empty] | 5 | High
Building 3 | [8 empty] | 4 | Medium to high
Building 4 | [8 empty] | 3 | Medium
[9 empty] | 2 | Low to medium
[9 empty] | 1 | Low
Package Number 2
Appin Reservoirs
Pressure Tunnel Shaft 10
Ashfield Reservoir
Avon - Berkeley
Balgownie Reservoir
Bellevue Hill Reservoir
Berkeley Reservoirs
Birchgrove SPS
Bonnyrigg Reservior
Eastlakes
Bulli
Buxton Reservoir
Camden Park Reservoir
Canterbury Park WPSA
Canterbury SPS
Caringbah Reservoirs
Carnes Hill Reservoir
Castlereagh Reservoir
Castle Reagh WPS 188
Cecil Park Reservoirs
Centennial Park Reservoir
Chapel Street Sewerage
Pressure Tunnel Shaft 4
Runnel Shaft 3
Coledale Reservoir
Condell Park Reservoirs
Couridjah WPS 197 & Vacant Land
Cranebrook Reservoirs
Cronulla STP10
Crown Street
Croydon Park Shaft Site And Depot
Dapto Reservoirs
Dapto Depot
Denham Court WPS
Dover Heights Reservoir
Drummoyne Reservoir
Pressure Tunnel Shaft 11
Earlwood Reservoir
Wast Hill Reservoir
Engadine Reservoir
Engadine Reservoir
Farmborough Hgts
Gerringong Reservoir
Green Hills Reservoir
Hammondville Reservoir
Hargrave Heights Reservoir
Heathcote Depot and Reservoir
Helensburgh Reservoir
Homebush Office
SPS 1006 Electrical
Illawarra Commercial
Illawong Reservior
Ingleburn Reservoir
Jamberoo Reservoir
Johnstons Creek SWC
Katoomba Business Office
Kembia Heights
Kenny Hill Reservoir
Kentlyn Reservoir
Kiama Town Reservoir
Kaima West Reservoir
Kaima WPCP
Kurnell Reservoir
Wiley Park Res No 0174, 0249, WPS 0107
Lakemba WPS & Depo
Leichhardt SPS
Leppington Reservoir
Leumeah Reservoir
Liverpool Commercial
Liverpool Reservoir
SPS 1088 Liverpool
Liverpool STP 9
Loftus Reservoir
Lucas Heights Reservoir
Lugamo Reservoir
Maianbar Reservoir
Mangerton Reservoir
Maroubra Reservoir
Pressure Tunnel Shaft 9
Marrickville Valley SWC
Menai Reservoir
Metropolitan Catchment Area
Milperra Bosster Station
Milperra Reservoir
Minto Reservoir
Minto WPS
Miranda Depot
Mount Keira Reservoirs
Mount Keira WPS
Mount Kembla Reserv oir
Mt Pritchard Reservoir / Willows Child Care
Mount Nebo
Mount Pleasant Reservior
North Georges River Submain
SPS 101
Leichhardt Civil Maintenance Depot
Oak Flats Reservoir
Panania Reservoir
Penshurst Reservoirs
Petersham Reservoir
Picton Reservoirs
Picton Sewerage Scheme
Potts Hill Pipelines
Potts Hill Reservoir
Prestons Reservoir
Raby Reservoirs
Randwich Reservoir
Rosemeadow Reservoir
Saddleback Reservoir
Scarborough Reserboirs
Shellharbour STP
Shellharbour SPS
Shellharbour WPCP
South Campbelltown Reservoirs
South Randwich Reservoirs
SPS 1113
SPS 112 & Sans Souci Carrier
SPS 116e
SPS 119
SPS 120
SPS 121
SPS 233
SPS 125e
SPS 126
SPS 134
SPS 135
SPS 136
SPS 138
SPS 143
Wollongong STP
SPS 146
SPS 161
SPS 164
SPS 166e
SPS 167e
SPS 168e
SPS 169
SPS 170e
SPS 171e
SPS 172
SPS 176
SPS 177
SPS 182
SPS 187
SPS 190
SPS 192
SPS 193
SPS 196
SPS 197
SPS 205e
SPS 207
SPS 21
SPS 211
SPS 214e
SPS 216
SPS 217 & East Hills Submain
SPS 22
SPS 220
SPS 223e
SPS 236
Bellambi
SPS 245
SPS 247
SPS 248
SPS 249
SPS 252e
SPS 255
SPS 268
SPS 269
SPS 271
SPS 274
SPS 284
SPS 287
SPS 288
SPS 289
SPS 290
SPS 214
SPS 293
SPS 296
SPS 297
SPS 298
SPS 30
SPS 308
SPS 309
SPS 310
SPS 314
SPS 318
SPS 321
SPS 322
SPS 323
SPS 325
SPS 326
SPS 327
SPS 329
SPS 330
SPS 333
SPS 334
SPS 335
SPS 336
SPS 337
SPS 338
SPS 340
SPS 341
SPS 342
Shellharbour STP
SPS 345
SPS 346
SPS 352
SPS 354
SPS 355
SPS 356
SPS 360
SPS 632
SPS 363
SPS 371
SPS 372
SPS 376
SPS 377
SPS 380
SPS 381
SPS 382
SPS 385
SPS 387
Huntley Street Depot, Alexandria
SPS 390
SPS 394
SPS 397
SPS 4
SPS 400
SPS 402
SPS 403
SPS 404
SPS 406
SPS 409
SPS 410
SPS 411
SPS 412
SPS 415
SPS 430
SPS 431
SPS 432
SPS 433
SPS 441
SPS 443
SPS 444
SPS 445
SPS 448
SPS 45
SPS 453
SPS 46
SPS 461
SPS 463
SPS 464
SPS 466
SPS 468
SPS 469
SPS 470
SPS 476
SPS 477
SPS 479
SPS 48
SPS 480
SPS 481
SPS 482
SPS 484
Shellharbour WPCP
SPS 5
SPS 50
SPS 500
SPS 501
SPS 502
SPS 506
SPS 507
SPS 513
SPS 514
SPS 515
SPS 53
SPS 534
SPS 539
SPS 540
SPS 544
SPS 557
SPS 558
SPS 559
SPS 560
SPS 563
SPS 567
SPS 568
SPS 569
SPS 58
SPS 597
SPS 604
SPS 605
SPS 606
SPS 607
SPS 609
SPS 612
SPS 614
SPS 62
SPS 63
SPS 630
SPS 635
SPS 636
SPS 64
SPS 642
SPS 643
SPS 648
SPS 649
SPS 65
SPS 650
SPS 651
SPS 652
SPS 655
SPS 66
SPS 660
SPS 662
SPS 663
SPS 667
SPS 67
SPS 670
SPS 676
SPS 73
SPS 74
SPS 78 & Depot
SPS 80
SPS 81
SPS 83
SPS 84
SPS 85
SPS 86
SPS 87
SPS 888
SPS 899
SPS 90
SPS 900
SPS 901
SPS 906
SPS 91
SPS 913
SPS 914
SPS 915
SPS 916
SPS 918
SPS 919
SPS 920
SPS 922
SPS 927
SPS 93
SPS 934
SPS 969
SPS 98
SPS 984
SPS 985
SPS 987
SPS 99
SPS 993
SPS 995
St Marys WPCP
Stanwell Park Break
Stanwell Tops
Stoney Creek Reservoir
Stormwater Pumping
Sugarloaf WPS
Sutherland Reservoirs
Sutherland SPS
Tahmoor WPS
Thirlmere Reservoir
Thirroul Reservoirs
Turramurra WPS
Upper Avon to Upper Cordeaux Connection
Vaucluse Reservoirs
Villawood Booster Station & WPS
Warragamba Catchment Areea
Warragamba North Reservoir
Waverley Reservoirs
West Camden WPCP
West Fairfield Reservoir
Wetherill Park Reservoir
Wongawilli Reservoir
Woollahra Reservoir
Woonona Heights Reservoir
Allawah Reservoir R001
WPS 123
WPS 131
WPS 150
WPS 153
WPS 173
WPS 187
WPS 195 Rosemeadow
WPS 210
WPS 242
WPS 81
Hoxton Park WPS
WPS 1008
West Dapto Stop Valve Bypass
WPS 1082 Homebush
SPS 1012
1007 Dapo
673 Harrington Park
275 Helensburgh
Wiley Park Elevated
Port Kembla WPCP
Potts Hill Elevated
SPS 589
Bulli Reservoir
SPS 1098
SPS 619 Bundeena
SPS 622 Bundeena
SPS 623 Maianbar
SPS 624 Maianbar
SPS 628 Maianbar
SPS 324 Burranbeer
SPS 681 Gerringong
SPS 683 Gerringong
SPS 684
SPS 1116 Gerringong
SPS 684
SPS 616 & SPS 688 Bundeena
SPS 776
WPS 32 Lungamo
Kembla Heights Reservior
Lower Thirroul Reservoir
Helensburg Reservoir
Potts Hill Booster Station
SPS 780
SPS 781
WPS 332 Adderley
SPS 1001
SPS 764
Georges River Program
Voyager Point Reservoir
Warragamba WPS 225
Megarritys Creet WPS

## Impt - wastewater
CRITICALITY RANKING SYSTEM - WASTEWATER
|  | A | B | C | D | E | F | G
| ISSUE | Potential Impact of failure on Life, Community, Property | Location | Loss of Service | Potential Impact on Environment | Size of Catchment Serviced | Cost of Failure | Site Function
Criticality Grade | Weighting | 130 | 40 | 100 | 100 | 30 | 80 | 20
1 | 1 | No risk to community and property | Low use Parks and open spaces, rural road sides | Complete service maintained by alternative means | No risk to the environment | Less than 10 Ha | Less than $25,000 | Equipment storage
2 | 3 | Minimal risk to public health, isolated cases of property damage. | Urban local road sides | Minor loss of service | Minor damage to environment lasting less than two days, minimal ecosystem damage. | 10 to 30 Ha | $25,000 to $100,000 | Offices
3 | 5 | Personal injury and sickness possible, minor damage to property, several properties flooded. | Urban areas, schools and public facilities | Service reduced but maintained without community restrictions | Environmental damage effects lasting up to one week, some damage to ecosystems | 30 to 50 Ha | $100,000 to $500,000 | Pumping station
4 | 7 | Personal injury and sickness likely, community access partially restricted, moderate damage to property, some habitable or commmercial floors flooded, together with some properties. | Civic parks, High density urban areas, commercial centres | Service severely reduced, community restrictions required | Environment and ecosystems affected for up to 3 months | 50 to 100 Ha | $500,000 to $1,000,000 | Sewage storage / detention facility
5 | 10 | Widespread personal injury and sickness likely, community access restricted, serious damage to property, several floors flooded, together with more properties. | Central business district, health facilities | No service until repaired or replaced | Environment and ecosystem damage effects lasting beyond three months | Greater than 100 Ha | Greater than $1,000,000 | Open ponds, treatment facility
Notes | In the context of property assets consider:-
| A | Potential Impact of failure on Life, Community, Property |  | The consequences at the site and beyond of loss of the asset resulting from damaging events such as (but not limited to) fire, act of vandalism, terrorism, structural failure, etc.
| B | Location |  | The asset is located in an area conforming with the location description
| C | Loss of Service |  | The consequence on the continuation of the wastewater service if the asset is damaged or lost.
| D | Potential Impact on Environment |  | The consequential environmental impact arising from a loss of the asset
| E | Size of Catchment Serviced |  | Catchment area serviced by the facility where the asset is located
| F | Cost of Failure |  | A rough order of cost assessment of costs arising from the loss (or damage) of the asset. Includes asset replacement costs (response, demolition, replacement, etc) AND consequential damage costs, reparation to neighbours, repair, and reinstatement
| G | Site Function |  | Principle activities occuring at the site of the building
Asset | means | Building (storage shed, workshop, office, laboratory, facility), security fence, access road and carpark, retaining walls, etc.

## Impt - water supply
CRITICALITY RANKING SYSTEM
|  | A | B | C | D | E | F | G
| ISSUE | Potential Impact of failure on Life, Community, Property | Location | Loss of Service | Potential Impact on Environment | Number of Customers Serviced | Cost of Failure | Site Function
Criticality Grade | Weighting | 130 | 40 | 100 | 30 | 100 | 80 | 20
1 | 1 | No risk to community and property | Low use Parks and open spaces, rural road sides | Low use Parks and open spaces, rural road sides | No risk to the environment | Less than 10 | Less than $25,000 | Storage
2 | 3 | Minimal risk to public health, isolated cases of property damage | Urban local road sides | Urban local road sides | Minor damage to environment lasting less than two days, minimal ecosystem damage. | 10 to 100 | $25,000 to $100,000 | Offices
3 | 5 | Possible public health risks, minor damage to property | Urban areas, schools and public facilities | Urban areas, schools and public facilities | Environmental damage effects lasting up to one week, some damage to ecosystems | 100 to 1,000 | $100,000 to $500,000 | Closed reservoir
4 | 7 | Public health consequences likely, moderate damage to property | Civic parks, High density urban areas, commercial centres | Civic parks, High density urban areas, commercial centres | Environment and ecosystems affected for up to 3 months | 1,000 to 10,000 | $500,000 to $1,000,000 | Pumping station
5 | 10 | Widespread public health consequences likely, serious damage to property | Central business district, health facilities | Central business district, health facilities | Environment and ecosystem damage effects lasting beyond three months | Greater than 10,000 | Greater than $1,000,000 | Open reservoir, treatment facility
Notes | In the context of property assets consider:-
| A | Potential Impact of failure on Life, Community, Property |  | The consequences at the site and beyond of loss of the asset resulting from damaging events such as (but not limited to) fire, act of vandalism, terrorism, structural failure, etc.
| B | Location |  | The asset is located in an area conforming with the location description
| C | Loss of Service |  | The consequence on the continuation of the water supply service if the asset is damaged or lost.
| D | Potential Impact on Environment |  | The consequential environmental impact arising from a loss of the asset
| E | Number of Customers Serviced |  | Number of customers serviced by the facility where the asset is located
| F | Cost of Failure |  | A rough order of cost assessment of costs arising from the loss (or damage) of the asset. Includes asset replacement costs (response, demolition, replacement, etc) AND consequential damage costs, reparation to neighbours, repair, and reinstatement.
| G | Site Function |  | Principle activities occuring at the site of the building
Asset | means | Building (storage shed, workshop, office, laboratory, facility), security fence, access road and carpark, retaining walls, etc.

## Financials
20 Year Expenditure Profile
| Annual Expenditure |  |  |  |  | 5-year blocks
Expenditure by Category | Year 1 | Year 2 | Year 3 | Year 4 | Year 5 | Yrs 1 to 5 | Yrs 6 to 10 | Yrs 11 to 15 | Yrs 16 to 20 | Total 20 Yrs
| (Expenditure $'000) |  |  |  |  | (Expenditure $'000) |  |  |  | Expenditure
CAPEX
Renewal programme | 815 | 0 | 5.865 | 0 | 0 | 820.865 | 602.388 | 95 | 151.435 | 1669.688
Refurbishment programme | 500 | 100 | 100 | 100 | 100 | 900 | 350 | 400 | 450 | 2100
Modernisation | 200 | 100 | 100 | 150 | 200 | 750 | 0 | 0 | 0 | 750
0
Acquisitions | 150 | 200 | 250 | 300 | 0 | 900 | 800 | 1000 | 1200 | 3900
demand and new services | [9 empty] | 0
Sub-Total CAPEX | 1665 | 400 | 455.865 | 550 | 300 | 3370.865 | 1752.388 | 1495 | 1801.435 | 8419.688
OPEX
Planned maintenance | 100 | 110 | 110 | 120 | 120 | 560 | 600 | 600 | 600 | 2360
(inc routine maintenance)
Consequential Opex | 10.5 | 19.5 | 30 | 43.5 | 49.5 | 49.5 | 73.5 | 103.5 | 139.5 | 366
Deferred maintenance | 250 | 350 | 0 | 0 | 0 | 600 | 0 | 0 | 0 | 600
Asset disposals | 0 | 0 | 50 | 50 | 0 | 100 | 0 | 0 | 0 | 100
Sub-Total OPEX | 360.5 | 479.5 | 190 | 213.5 | 169.5 | 1309.5 | 673.5 | 703.5 | 739.5 | 4839
Total Expenditure | 2025.5 | 879.5 | 645.865 | 763.5 | 469.5 | 4680.365 | 232990 | 232990 | 232990 | 13258.688